Section 6: Employer’s Requirements

### Scope of Supply of Plant and Services

### Context

The Enhancing Climate Resilience and Food Security Project (the Project), financed by the Asian Development Bank (ADB, Project Nr. 57002-001), aims at building resilience in selected islands, including strengthening capacity and awareness to plan, adapt, and respond to climate change through improved early warning systems. One of the Project’s subprojects is the improvement of the Maldives weather observation system and associated capacity development, with the aim to establish a new radar weather observatory system in Addu City covering the southern region of the country. It will be linked to the existing early warning, forecasting, and other relevant systems with due consideration of compatibility with the existing or planned other radar systems in Maldives.

The current Addu Meteorological Observatory is located in Addu City atoll (Figure 1) and is managed by the Maldives Meteorological Service (MMS), part of the Ministry of Tourism and Environment (MOTE). It is the local provider of observation data of the atmosphere, of ocean and of hydrology in the atoll of Addu. In Addu, MMS operates a synoptic and aeronautical weather observing station, a radio-sounding station and a tide gauge. The MMS facilities are presently located on Gan International airport, north of the runway (Figure 2). There is a plan to move these facilities across the runway to the ocean side of the island (Figure 3).

The Project is financing the installation of a radar system on Addu, including a Doppler Weather Radar (DWR) and related civil works, peripherals, interfaces and software, which will be under the operational responsibility of MMS. The DWR in Addu will allow for production of detailed pictures of rain cells within a radius of up to 500 km, with images separated by intervals of a few minutes and with a grid size of typically 1 km. This will be a key input for improving the weather forecasters’ understanding of the overall weather situation and preparing more accurate heavy rain and strong winds occurrence predictions. The data could also feed into numerical weather prediction models.

The Client of the Contract resulting from this call for tenders will be called the Employer. It will be the Government of Maldives, which includes MCCEE, the Project Management Unit (PMU) located in MCCEE, MMS and any other delegated authority as well.

For technical and contractual purposes, the Employer shall appoint a Project Manager to represent the Employer. Upon agreement with the Client, the Employer may delegate the authority/responsibility of the Project Manager to the "Team Leader of the Construction Supervision Consultant", a Firm that is planned to be hired under the Project.

The terms ‘the Contractor’ by and large will include the Lead firm, associate or JV partners, Designer, Civil works sub-contractors, any other sub-contractor, any supplier, any manufacturer, or any service provider etc., including the personnel appointed (contractual/employee/ad-hoc appointee etc.). The Prime Lead Firm will assume the overall responsibility of the contract. Any activity/delivery out of the regular business of the prime/lead firm can be allowed to Sub-contractor(s). The Prime Lead Firm will bear overall responsibility of the contract and coordination/compliance by its Specialized Sub-contractors.

### General

#### General Doppler Radar requirements

The Doppler Weather Radar basic operational requirements are to provide information related to:

- Full radar coverage over the southern atolls (Addu, Fuvahmulah, Huvadhu Atoll and part of Laamu Atoll)

- Weather monitoring

- Nowcasting of high impact weather

- Heavy rain

- Cloud bursts

- Thunderstorms

- Gusty winds

- Sea conditions

- Wind shear

- Data assimilation by Numerical Weather Prediction (NWP) models

- Data and products transmitted to Hulhule

- Radar composite in Hulhule

- Display at Gan met office (back-up)

The design policy of the equipment is to deliver an ensemble suitable for use as meteorological radar facility and to become an operational element for weather observation and forecasting. This ensemble will include the radar building and the DWR, together with the MMS Gan Observatory facilities located nearby, where space and personnel will be available for observation, maintenance and back-up to Malé, and the equipment installed in the MMS Malé Forecasting office, where forecasts and warnings will be made.

In view of fulfilling these operational requirements, the Contractor shall design and install a system complying with the following capacities:

- To be a Doppler system suitable for both quantitative rainfall, radial wind velocity and air-turbulence observation in precipitation areas, to accurately observe severe weather conditions.

- To provide high resolution and high frequency observations of radar reflectivity up to a distance of 500 km, and of radial wind velocity and spectrum width up to a distance of 250 km.

- To be S Band (wavelength: approximately 10 cm), suitable for precipitation observations over a very wide area, in real time.

- To be suitable to 24 hours a day automatic operation with possibility of remote control and operation programming from MMS in Malé, with backup in Addu MMS Observatory.

- To have a scanning capacity of 10 elevation angles with the 3 spectral moments acquired in 5 minutes or better.

- To have a detection capacity of 0 dBZ at 100 km distance.

- To have data processing and display capabilities suitable for accurate thunderstorms monitoring and weather forecasting.

- To be compatible with the local environment.

- Spare parts and consumables can be easily procured and replaced.

- To minimize the recurrent costs to MMS of the operation, maintenance and repair.

- To include state of the art capacity of adjusting the accuracy of the radar data through calibration.

- To provide the necessary data for meteorological work to be performed effectively and efficiently in the forecasting office in Malé, and, as a back-up, in Addu Observatory.

- To be suitable for MMS’s 24hours/day 7 days/week work schedule of observations and forecasting.

- To operate using 400V±20%, 3 Phase, 50Hz or 220V±20% Single Phase, 50Hz, power.

- To have the necessary power supply back-up equipment (diesel generator, radar power backup unit, UPS, auto voltage regulator, etc.) for performing round-the-clock meteorological services.

- To be sufficiently robust to withstand extreme weather and permit the performance of uninterrupted radar observation and the supply of weather forecast and warnings even under severe weather.

- To minimize potential lightning damage.

- To include all necessary testing and calibration equipment as well as spare parts which may be necessary for a duration of 5 years.

Table 1 shows the geographic distribution of equipment and software of the Addu Radar System subproject.

Table 1: Main components of the radar system and geographic distribution

|  | New Radar building | Addu MMS Observatory | Malé MMS Headquarters |
| --- | --- | --- | --- |
| Radar tower building | x |  |  |
| Doppler Weather Radar | x |  |  |
| Control and display workstations | x | x | x |
| Data communication and archiving | x | x | x |
| Data integration into MESSIR NEO |  |  | x |

The Radar building will host the radar unit (transmitter, antenna, antenna scanning mechanisms, radome, receiver, processing, Control and Display Workstation, sliding raw data archive and telecommunication devices). There is also a need in the radar tower of room for maintenance and calibration, and for power supply and other appliances, such as air conditioning.

The Addu observatory will host data processing elements, radar display and control capacity, data archiving, and adequate telecommunication capacity with Malé, back up radar data interpretation and forecasting capacity in case of breakdown at Malé. This will represent broadly two racks and two workstations. Enough space must also be allowed in the maintenance room of the Observatory building for radar interventions.

In the Malé MMS premises, telecommunication capacity, radar control, radar data display, radar products generation (including observations, forecasts and tailored products for the public of specific users), received data archive, interface to the central weather prediction system MESSIR NEO of MMS and upgrades to that system as necessary.

#### Radar building

The radar building will be installed south of the Gan airport runway, close to the proposed relocation place of the MMS Addu Observatory, as shown in Figure 3Figure 2.

The minimum floor area of each room of the radar building, the number of working staff, its function and the method of calculation are shown in Table 2. It should be noted that:

- There shall be no permanent staff in the radar tower, which operates automatically. However, there will be occasional staff presence and sufficient safe working space is necessary for calibration and maintenance purposes.

- It is assumed that the radar tower will also contain a 3-phase current transformer, electrical appliances, two power generators with sufficient fuel reserve, air conditioning and UPS.

- The tower shall not be a metallic tower, to avoid corrosion problems.

- The Contractor is requested to implement adequate measures to avoid flooding risk damage in the lower floor.

Table 2: Indicative calculation base for the rooms in the Radar building

| Name of room | Min area (m²) | Staff | Room Function | Calculation base |
| --- | --- | --- | --- | --- |
| Radome (roof) | 56 m² (the estimated diameter of the radome base is 8.5 m) | Max. 3 staff during maintenance interventions | Radar antenna and pedestal | Estimated radome diameter 11 m |
| Radar equipment room | 56 m² with 4 windows | Max. 3 staff during maintenance interventions | Installation space for antenna controller, transmitter, receiver, signal processor, Control and Display Workstation, dehydrator, wave-guide configuration, radar task controller, power distribution box, optical repeater, maintenance box, maintenance cabinet, measuring instrument cabinet, etc. | Operation and maintenance space for all the apparatuses described in the left column. |
| Appliances room | At least 70 m² (with 4m minimum ceiling height and adequate ventilation) | Max. 3 staff during maintenance interventions | 2 engine generators, service tanks, isolation transformers, power distribution boards, radar power back-up unit (UPS), air conditioning, and other electrical appliances | Generators and fuel tank would need about 40 m², and the remaining appliances 30m² |

- Addu MMS Observatory

The Addu MMS Observatory building is presently located north of the Gan airport runway, and there are plans to move it to the south of that runway, as shown in Figure 3. It is assumed for the Project that this relocation will not be done before the installation of the radar.

The MMS Observatory will be equipped with a Control and Display Workstation (CDS), similar to the ones installed in Addu Observatory and in Malé Forecasting service, performing the following functions:

- Connection with the radar tower for data reception and control transmission. The distance is of 1,700 m in straight line, across the runway.

- Transmission of the radar data to Malé, with all necessary ancillary data and radar control information

- Radar operation control, including full automated operation modes, as back-up to Malé.

- Digital radar signal processing and meteorological radar data display, with real time (from tower) and replay (from archive) capacities

- Archiving of Level II (radial Reflectivity, velocity, spectrum width and ancillary data) information to be transmitted to Malé, with a capacity for one year of sliding archive.

- A maintenance workshop, with the necessary room equipment and spares for the radar calibration and maintenance during 5 years.

Table 3: Addu Observatory building indicative space requirement

| Name of room | Min area (m²) | Staff (Nr) | Room Function | Estimation base |
| --- | --- | --- | --- | --- |
| Operations | 12 | 1 (part time) | Radar data processing, transmission and display. Radar back-up control. | May be shared with telecommunications, Observation and/or Forecasting rooms of the Observatory (2 racks and 2 workstations) |
| Maintenance | 25 | 3 | Radar calibration and maintenance | May be shared with the general maintenance room - Electronic and mechanical equipment and tools, electronic and power electronics bench, microwave and test bench |

#### Malé MMS Headquarters

The Malé MMS headquarters telecommunication and forecasting rooms will be equipped with a Control and Display Workstation (CDS) performing the following functions:

- Telecommunication with Addu observatory and the Radar building for radar data reception and radar control.

- Radar operation control, including choice of full automated operation modes, as master unit.

- Digital radar data processing and meteorological radar data display, with real time (from tower) and replay (from archive) capacities

- Archiving of Level II (radial Reflectivity, velocity, spectrum width and ancillary data) information received in Malé, with a capacity for one year of sliding archive.

- Permanent archiving of 5 years of all information received from Malé.

The Control and Display workstation shall be interfaced with the MESSIR NEO central telecommunication and data processing system which will be requested to perform the following tasks:

- Calibration of precipitation estimations of all Maldives weather radar with rain gages data as received from automatic weather stations under radar coverage.

- Compositing of all Maldives weather radar data received in Malé at 5 to 15 minutes user selectable intervals, with a horizontal resolution of 1 km.

- Prediction of rain cells movements up to 2 hours ahead.

- Tailoring of specific radar products, including precipitation totals (from 1 hr to 24 hours, heavy rain warnings, storm warnings, including if requested specific users’ products).

- Public Internet access to observed and predicted maps

- Transmission on request by Internet of observed and predicted precipitation on any location sufficiently well covered by radars.

- Transmission of radar data to the WIS2.0 (WMO Information System)

In addition to MESSIR NEO interface, manufacturers basic radar software should be able to support core functioning of the radar including basic visualization (eg: reflectivity and velocity maps), radar control and signal processing.  All raw data should be produced in NetCDF/CF , FM 301-2022 WMO-CF RADIAL and GRIB-2 format ready for utilization in other applications.

#### Radar operation modes

The radar operation will usually be entirely automatic, along sequences decided beforehand by the radar operator, depending on the meteorological situation. It is not recommended in operational conditions to take human control of the radar scanning, because the operator usually has no time to select and explore the most suitable locations and may miss critical developments out of his/her area of interest. The main operation modes to be available are the following:

- Watch mode: When there are no radar echoes in the radar range, it is preferable to shut down the equipment, to save energy and wear of components. It should be noted that magnetrons are expensive components and that their lifetime depends on the number of pulses which have been transmitted. When echoes may be present, the radar should go to another mode. This can be decided for instance by the forecaster, when precipitation appear on the GPM (Global Precipitation Measurement mission)  data, or from other source of information.

- Monitoring mode: when radar echoes are present, even at large distance, the system may operate in monitoring mode, performing only one low elevation PPI (Plane Position Indicator) scan every 15 minutes.

- CAPPI mode: Constant Altitude PPIs (CAPPI) may be repeated every 5 minutes over 360 degrees azimuth with a small number of successive elevation angles. It allows to display the echoes intensities at constant altitude and should be used as soon as echoes are present at less than typically 150 km.

- Other modes: RHI (Range-Height Indicator), Volume, Sector, sun calibration, Manual scan and more should also be available.

#### Scope of works to be undertaken by the Contractor

- Architectural design of the radar tower building, verified and stamped by a licensed engineer and architect (accredited by the Ministry of Construction, Housing and Infrastructure of the Maldives.)

- Civil engineering and construction.

- Electrical work.

- Air-conditioning and ventilation.

- Plumbing.

- Power supply intake, including backup diesel generators and UPS. Electricity connection to the nearest substation is responsibility of contractor.

- Telephone and Internet line connection.

- Radar system design and manufacturing.

- Radar system shipping and installation in the three locations.

- Basic Radar Software.

- Interfacing with MESSIR NEO system in Malé and ensuring that the specified functions are met.

- System maintenance during 10 years after completion.

#### Scope of works to be undertaken by the Employer

- Undertaking all necessary institutional and juridical procedures in Maldives.

- Securing the Project sites.

- Securing necessary permits for construction of the radar tower building and for the radar operation (including frequency allocation, building height clearance, power and Internet cables and hardware, including direct liaison between the radar building and the Addu Observatory).

- Handling import tax exemption procedures and to take necessary measures for import permits and customs clearances.

- Movement and relocation of any obstructions in the Project sites, if required.

- External and planting work, if necessary.

- Purchase of furniture which is not indicated in the drawings in this report, if required.

- Securing sufficient spaces at the proposed Project Sites (Radar building, Addu Observatory, MMS Malé premises) for temporary facilities such as contractor’s office, workshop, building materials storage, etc. needed for the construction work.

- Assigning sufficient number of trainees for the training program and cover their mission costs to the training sites, such as per diems, transportation, if any (including three participants from Addu).

- Providing necessary working space and facilities for training courses.

- Maintaining the radar building after its commissioning, including cleaning, preventive and corrective actions.

### Specifications

The required specifications described under this section cover:

- General specifications (GEN).

- The radar building, including power supply, access to Internet and air conditioning (RBG).

- The radar including the antenna, radome, transmitter, receiver and signal processing (DWR).

- The control and display workstations to be installed the radar building, in Addu Observatory and Malé headquarters (CDS).

- Data transmission (DTR).

- Interfacing with the Campbell Scientific MESSIR NEO central MMS processing system in Malé, and ensuring the operationality of multiple radars mosaicking and nowcasting products generation, including additional MESSIR NEO software developments for that purpose if necessary (CDP).

- Monitoring and maintenance (MMT).

- Training of MMS personnel (TRN).

- Deliverables and delivery schedule.

#### General specifications

Software and IT

GEN-01: The proposed software must be already marketed and proven in National Hydrometeorological Services or airport meteorological authorities.

GEN-02: Licenses for the application software provided shall not be limited in time.

GEN-03: Information systems must be designed as a virtualized solution.

GEN-04: The proposed systems must be operated and administered via a web-based graphical user interface to allow simplified deployment and management of IT equipment.

GEN-05: For security reasons, software solutions based on UNIX or LINUX operating systems are required.

Equipment

GEN-06: As much as possible, the proposed equipment must consist of standard equipment with on-site support services in the Maldives.

GEN-07: The equipment must be purchased, tested and integrated in the factory by the Contractor.

GEN-08: All supplies required for the project will be transported to the Maldives and installed by the Contractor.

GEN-9: Once the hardware equipment has cleared Maldivian customs upon presentation of an exemption certificate issued by the Ministry of Finance Planning, the Contractor will be responsible for storage and transport until the on-site installation of each piece of equipment, then its installation.

GEN-10: All equipment and cables required for the installation of the equipment will be deemed to be included in the Contractor’s offer and therefore provided by the Contractor at its expense.

Contractor’s responsibility

GEN-11: For factory activities requiring the presence of Maldivian personnel (training, testing and acceptance), the Contractor must provide airfare, ensure daily allowances for trainees and inspectors to cover accommodation and living expenses. All these costs will be detailed by the Contractor in its financial proposal.

GEN-12: All training activities requested within the present Contract will be organized under the responsibility of the Contractor’s and conducted in English.

GEN-13: Factory acceptance tests (FAT) and site acceptance tests (SAT) will be conducted in accordance with a detailed test plan and procedures provided by the Contractor and validated in advance by MMS.

GEN-14: Each system or equipment will only be declared operational after the completion and signature of the site acceptance tests (SAT).

GEN-15: Each system shall benefit from guarantee and support services up to 10 years starting from the date of completion.

GEN-16: The System will be integrated for a complete solution and an integrated implementation in the existing environment

GEN-17: The Contractor is responsible for systems integration by ensuring that all proposed components of the project are correctly interfaced with other systems.

#### Radar building (RBG)

Table 4: Radar building specifications

| Spec.Nr. | Subject | Requirements |
| --- | --- | --- |
| RBG-01 | Available space in the radar building rooms | Sufficient space to accommodate the radar equipment supplied under the Project, on the base of Table 2. |
| RBG-02 | Geographical coordinates | To be agreed with MMS at the design stage |
| RBG-03 | Reference ground level | A benchmark shall be determined during the topographic work, to be used as a reference for the construction |
| RBG-04 | Building height | To be agreed with MMS at the design stage (without radome) |
| RBG-05 | Structure | Reinforced concrete |
| RBG-06 | Wind pressure, with radome | The building, including the radome, should resist an average wind speed 200 km/h, with gusts at 250 km/h. |
| RBG-07 | Seismic resistance, with radome | Compliant with the Maldives building code |
| RBG-08 | Foundations | To be designed to ensure that horizontal deflection by wind is lower than 1/1,000 of the height of the building |
| RBG-09 | Roof | Should support a weight of 12 tons, corresponding the radome, the antenna and the antenna pedestal. |
| RBG-10 | Radar equipment room floor | The radar equipment room will have an access floor with a clearance of 15 cm for easy wiring of power and signal cables, trouble-free maintenance. An anti-static, heavy-duty access floor has been selected for the radar equipment room in which a high-power radar and equipment weighing up to 4 tons is to be installed. |
| RBG-11 | Ground floor | To be built high enough to avoid risk of water intrusion damage. The ground floor should support a total weight of 12 tons, including the fuel reserve. |
| RBG-12 | Stairway | A stairway of minimum 1.20 meter wide from the ground level to the upper rooms and to the roof under the radome shall be included. |
| RBG-13 | Hoist system | A hoist system shall be included, with the capacity to raise 300 kg loads from the ground up to the antenna pedestal level. |
| RBG-14 | Electrical Power supply | 400V, 3-phase, 4-wire, 50Hz, stabilized, with a capacity no less than 80 kVA |
| RBG-15 | UPS | 2 online redundant UPS with support time of 30 minutes minimum including radar, processing, transmission and air conditioning. |
| RBG-16 | Diesel generators | 2 generators of 20 kVA or more |
| RBG-17 | Fuel reserve | Sufficient for operating the radar continuously for 7 days |
| RBG-18 | Air conditioning | Humidity control inside the radome and temperature/humidity control in the radar equipment room. |
| RBG-19 | Internet fiber access minimum speed | 2 Mb/s each way |
| RBG-20 | Earthquake resistance | Maldivian building code standards |
| RBG-21 | Insulation | The building walls will be designed to minimize the electricity consumption by air conditioning, using glass wool for heat insulation in the radar room. |
| RBG-22 | Ceilings | Will include acoustic panels. |
| RBG-23 | Windows | There shall be 4 aluminum windows at each floor, oriented towards the cardinal points. |
| RBG-24 | Antenna and radome installation | Necessary infrastructure and interfaces shall be designed in agreement with the radar and radome manufacturers. |
| RBG-25 | Fence (TBC) | The building shall have a security fence or other suitable barrier to prevent the entrance by animals and unauthorized persons, with a height of 3 m plus barbed wire, with two 4 m wide sliding gates. |
| RBG-26 | Design load | Roof top: 12.0 tons Radar room: 4.0 tons Electricity and power supply room: 10.0 tons |
| RBG-27 | Telephone system | Telephone line, terminal box and telephones with intercom shall be installed in each room |
| RBG-28 | Alarm system | An alarm system shall be installed with connection to the Addu Observatory through both GSM and Internet, providing the following warnings: - failure of air conditioning units in the radar room - failure of the radar back-up unit - overheating of generators - breaker tripping of distribution boards - fire |
| RBG-29 | Fire detectors | Appropriate fire detectors will be supplied in all rooms |
| RBG-30 | Grounding system | Grounding cables will be present on all floors and connected to the terminal box for earthing. |

#### Doppler Weather Radar (DWR)

Table 5: Doppler Weather Radar specifications

| Spec.Nr. | Subject | Requirements |
| --- | --- | --- |
| General |  |  |
| DWR-01 | Reflectivity max. observation range | 500 km |
| DWR-02 | Velocity and spectrum width max. observation range | 250 km |
| DWR-03 | Minimum detectable signal (MDS) | -113 dBm |
| DWR-04 | Sensitivity | 0 dBZ at 100 km |
| DWR-05 | Volume scan capacity | 10 elevation 360° azimuth scans with all 3 first moments acquired in 5 minutes or less |
| Antenna |  |  |
| DWR-06 | Antenna type | Parabolic with feed horn |
| DWR-07 | Diameter | 8 m at 10% |
| DWR-08 | Beamwidth | 1° maximum at 3 dB |
| DWR-09 | Polarization | Linear horizontal |
| DWR-10 | Gain | 43 dB or more without radome |
| DWR-11 | Azimuth range | 360° with continuous rotation capacity |
| DWR-12 | Elevation range | -2° to 90° |
| DWR-13 | Max side lobe level | -23 dB without radome |
| DWR-14 | Max antenna rotation speed | 4 rpm or more |
| DWR-15 | Max Elevation drive time from 0° to 90° | 30 s |
| DWR-16 | Max time from maximum speed in Azimuth to complete stop | 5 s |
| DWR-17 | Antenna pointing accuracy | .1° |
| DWR-18 | Antenna alignment | The antenna mount should be equipped with a leveling system to ensure its horizontal alignment. Readers shall be included with an accuracy of 0.1 degree or better. |
| Radome |  |  |
| DWR-19 | Radome type | Spherical, foam sandwich, white, rigid. Shall include hatches for the maintenance of obstruction lights, with a portable ladder for access. |
| DWR-20 | Radome 2 ways max attenuation | .6 dB in dry conditions |
| DWR-21 | Wind resistance, with radome | Average 200 km/h, with gusts at 250 km/h |
| DWR-22 | Coating | Hydrophobic coating |
| DWR-23 | Lightning protection | Lightning rod on top of the radome, with grounding compliant to local regulations. The lightning protection should not create artifacts in the radar data. |
| DWR-24 | Obstruction lights | Solar powered waterproof obstruction lights according to ICAO prescriptions. |
| Transmitter |  |  |
| DWR-25 | Transmitter type | Coaxial magnetron |
| DWR-26 | Modulator | Solid state |
| DWR-27 | Transmission frequency | 2,700 to 3,000 MHz |
| DWR-28 | Transmitted power (peak) | 500 kW |
| DWR-29 | Phase stability | .2 ° |
| DWR-30 | Pulse width | Selectable from 1 to 2 microseconds |
| DWR-31 | Pulse repetition frequency (PRF) | Selectable between 300 and 2400 Hz, including staggered PRF for velocity de-aliasing |
| DWR-32 | Dehydrator | The wave guides shall be equipped with a ventilation pressure dehydrator to reduce wave propagation loss. |
| Receiver and signal processing |  |  |
| DWR-33 | Receiver dynamic range | 110 dB |
| DWR-34 | Quantization dynamic range | 80 dB with +/- 1dB linearity. |
| DWR-35 | Quantization resolution | 14 bits I and Q signals. |
| DWR-36 | Number of range gates | Adjustable and programmable up to 1024 depending on selected range resolution and maximum distance of observation .. |
|  | Sampling rate | Adjustable between 1 MHz and 150 kHz. |
| DWR-37 | Fast Fourier transform and pulse-pair processing | Number of samples selectable and programmable from 64 to 256 |
| DWR-38 | Observation range | Closest data at no more than 75 to 300 m (depending on pulse width) up to the maximum distance allowed by the selected PRF. |
| DWR-39 | Clutter suppression | High pass filtering and provisions for eliminating non meteorological echoes, especially sea clutter. |
| DWR-40 | Velocity de-aliasing | Staggered PRF |
| DWR-41 | Digital output (Level II data) to the Radar transmission unit | Reflectivity (Z), Doppler velocity (V) and Spectrum width as a function of distance, Azimuth angle, Elevation angle and time, with 8 or 16 bits resolution |
| DWR-42 | Time reference | GPS NTP server |
| DWR-43 | Recording and archiving capacity | Digital composite video I and Q signals (14 bits) from 1024 range gates, with all necessary ancillary information (time, Az, El, radar operation parameters, …) for selected periods, with a recording capacity of 1 Tbyte. |
| Radar control and data exchange unit |  |  |
| DWR-44 | System | Intel Core I9 -10900 or better, with 10-20 cores, 2.8 GHz clock base and 5.2 GHz turbo, 20 MB of memory cache |
| DWR-45 | Memory | 2TB NAS storage |
| DWR-46 | Monitor | 2 LED monitors 32 inches full HD |
| DWR-47 | LAN interface | Ethernet |
| DWR-48 | Software | Operating system: UNIX or LINUX based |
| DWR-49 | Radar control functions | Operating the radar system according to the requests of the Control and display workstations (CDS) of Malé (principal), Addu (Back-up) and Radar building (testing) |
| DWR-50 | Radar monitoring and calibration functions | - All provisions shall be made to include programmable and automatic overall system calibration, including receiver linearity and dynamic range, transmitted power and system noise figure, with the necessary equipment and software provided with the System, and to update radar parameters accordingly. - Temperatures shall be monitored in the sensitive parts of the radar system, providing alerting messages to the operator in case of danger. - Software for automatic on demand sun calibration (antenna pointing and noise temperature) shall be provided. - Display of raw data and detailed radar status |
| DWR-51 | Telecommunication functions | - Reception of Digital output (Level II data) from the Signal processor (LEVEL II data). Transmission of LEVEL II radar data to the Control and display workstations, together with radar operation parameters, and reception of command-and-control information from those stations. |
| DWR-52 | LAN Interface | Ethernet IEEE 802.3, 8 ports |
| DWR-53 | Optical repeater | Connection to the 3 Control and display stations (Control and data information) and to MESSIR NEO (data only). |
| DWR-54 | Color printer | Inkjet type A3, with 1,200 dpi resolution, 7 pictures per minute printing speed, with LAN Interface |

#### Control and display workstations (CDS)

The main functions of the three CDS shall be:

CDS-01	Operation monitoring of the radar system.

CDS-02	Remote control of the radar system, including scheduling of automatic radar operation. This control is in the hands of the Malé CDS, with the possibility of takeover by the Addu Observatory CDS as back up and by the radar tower CDS for maintenance purposes.

CDS-03	Monitoring of the radar observation data for quality control.

CDS-04	Alteration of the radar system configurations.

CDS-05	Adjustment of the signal processing.

CDS-06	Monitoring of the operation environment (equipment and room temperature) in the radar equipment room.

CDS-07	Remote control of air conditioning systems in the radar equipment room.

CDS-08	Remote control of engine generators.

CDS-09	Security monitoring of the radar building (against fire and intrusion).

CDS-10	Reception and recording of radar data (LEVEL II).

CDS-11	Radar products generation as mentioned in Table 4.

CDS-12	Display processing and data visualization with adequate GIS overlays for observation and forecasting applications. The system must have its own GIS and must also be able to connect to an external GIS via the latest OGC protocols.

CDS-13	Web server capacity.

CDS-14	In Addu radar building and in Addu Observatory, one year sliding archive of LEVEL II radar data, with possibility of replay of archived data.

CDS-15	In Malé only, archival of 5 years of radar data

Table 6: Control and display workstations specifications

| Control and display workstations (CDS) |  |  |
| --- | --- | --- |
| Spec.Nr. | Subject | Requirements |
| CDS-16 | System | Intel Core i9-11980HK or better, with 8 cores, 5 GHz turbo clock, 24 MB of memory cache |
| CDS-17 | Memory | 2 TBytes |
| CDS-18 | LAN interface | Ethernet |
| CDS-19 | Operating system | UNIX or LINUX based with latest configuration |
| CDS-20 | Language | Python or C |
| CDS-21 | Formats | NetCDF, OPERA ODIM |
| CDS-22 | Rain rate estimation | Z-R relationship, user selectable |
| CDS-23 | UPS | Compact UPS, 1kVA or more, for at least 5 minutes operation time |
| CDS-24 | LAN Interface | Ethernet IEEE 802.3, 8 ports |
| CDS-25 | Archival | In Malé only, Level 5 Redundant Array of Independent Discs with a storage capacity of 5 years of LEVEL II radar data, and replay capacity on the CDS |
| CDS-26 | Monitor | 2 LED monitors 32 inches full HD |
| CDS-27 | Color printer | Inkjet type A3, with 1,200 dpi resolution, 7 pictures per minute printing speed, with LAN Interface |
| CDS-28 | Clutter suppression function | From map overlays |

The main user’s observation products requested at the three dedicated Control and Display radar workstations and available at the forecaster’s request are listed in Table 7.

CDS-29:	When not displayed automatically, any of these products shall be produced and displayed in less than 10 seconds at the forecaster’s request (when applicable, depending on the scanning mode used), and on a 1 km x 1 km mesh.

CDS-30:	The meteorological radar data display system will be designed to store data files of the radar pictures as binary data of hourly accumulated precipitation data of not more than 1.0 km mesh.

CDS-31: 	A JPEG image output of these displays shall be available.

Table 7: Observation products requested at the three dedicated Control and Display radar workstations and available at the forecaster’s request

| Spec.Nr | Radar products | Related parameters |  |  |  |  | Maximum selectable Range (km) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Reflectivity (Z) | Doppler velocity (V) | Spectrum width (σ) | Rain rate (RR) | Other |  |
| CDS-32 | PPI display | x | x | x | x |  | 50-500 |
| CDS-33 | RHI display | x | x | x | x |  | 50-100 |
| CDS-34 | Heavy rainfall warnings and outputs (based on Z-R relationship) |  |  |  | x |  | 20-200 |
| CDS-35 | Accumulated rainfall on user selected areas and time periods and warnings issuance (based on user selectable Z-R relationship) |  |  |  | x |  | 20-200 |
| CDS-36 | Warnings issuance for high Doppler velocities, wind shear and/or large spectrum width, depending on thresholds fixed by the operator. | x | x | x | x | x | 200 |
| CDS-37 | Vertical wind profile (VAD) |  | x |  |  |  |  |
| CDS-38 | CAPPI display | x | x | x | x |  | 50-200 |
| CDS-39 | Echo tops display |  |  |  |  | x | 50-200 |
| CDS-40 | Cross sections | x | x | x | x |  | 50-200 |
| CDS-41 | Vertically integrated liquid |  |  |  |  | x | 50-200 |
| CDS-42 | 3-dimensional data display | x | x | x | x |  | 50-200 |
| CDS-43 | Echoes movement extrapolation up to 2 hours ahead, with time-lapse video display. | x |  |  |  |  | 50-200 |

The radar operation will be in general entirely automatic, along sequences decided beforehand, the operation mode depending on the meteorological situations.

CDS-44: 	Mosaicking radar scan mode: at the operator’s request, the system should be able to operate in the mosaicking mode, which is best suited to build composite pictures with the Malé radar and potential additional radars in the Northern atolls. In this scan mode, the radar operation will be entirely automatic, along sequences decided beforehand, in order to optimize the quality of the composite pictures. The CDS software shall allow programming the repetition every 5 to 30 minutes (selectable) of 1 to 10 (selectable) 360° Azimuth scans at different (selectable) Elevation angles with the following adjustable parameters:

- Elevations (degrees): selectable between 0 to 30.

- Azimuth rotation rate (RPM): .4 to 4, may vary depending on elevation angle.

- PRF: selectable, may vary depending on elevation angle.

- In the Mosaicking radar scan mode, it shall be possible to choose for mosaicking a CAPPI display representation, on a 1 km mesh, with a radar range up to 500 km, and including ground and sea clutter rejection based on interpretation of data at different elevation angles.

#### Data transmission (DTR)

Table 8: Data transmission line specifications

| Spec.Nr. | Transmission line | Nature | Scope |
| --- | --- | --- | --- |
| DTR-01 | Between radar building Control and Data Exchange unit and radar building Control and Display Workstation (CDS Nr.1) | LAN 2Mb/s | Monitoring and control, LEVEL II data under NetCDF protocol |
| DTR-02 | Between radar building Control and Data Exchange unit and Addu Observatory Control and Display workstation (CDS Nr.2) | Optical fiber liaison (max 2000 m - TBC) 2Mb/s | Monitoring and control, LEVEL II data under NetCDF protocol |
| DTR-03 | Between radar Control and Data Exchange unit and Malé MMS headquarters Control and Display workstation (CDS Nr.3) | Public Internet liaison 2Mb/s | Monitoring and control, LEVEL II data under NetCDF protocol |
| DTR-04 | Between Radar building Control and Display workstation and MESSIR NEO | LAN 2Mb/s | LEVEL II data under NetCDF or OPERA HDF5 protocol |
| DTR-05 | Between Malé MMS headquarters Control and display workstation and central MMS archiving facility (if applicable) | LAN | LEVEL II data |
| DTR-06 | From Malé MMS headquarters Control and display workstation and selected users | Internet | Transmission of selected products |

DTR-07	The Contractor shall take the necessary provisions in order that the protocol used by the CDS be fully compatible with MESSIR NEO.

DTR-08	The protocols utilized for radar monitoring and control shall be provided and disclosed by the Contractor.

#### Central data processing (CDP)

The compositing of data from different radars, the nowcasting applications and the tailoring of most user products will be done by the new telecommunication and data processing system MESSIR NEO, produced by Campbell Scientific/Corobor and recently installed at the MMS Malé forecasting office. MESSIR NEO has the capacity to ingest the radar data, to develop radar mosaics of images coming from different radars, to predict the movements of radar echoes, to display and process radar data together with other sources of observations and model outputs, and to make tailored products and warnings. Table 6 provides the list of radar related products to be produced by MESSIR NEO, using the data received from the radar and for other sources.

CDP-01	The Contractor is requested to develop and install the necessary software in MESSIR NEO when it is not already available in the configuration installed beforehand in Malé.

Table 9: MESSIR NEO expected radar related mosaicking and nowcasting products

| Spec.Nr. | Product | Requirements |
| --- | --- | --- |
| CDP-02 | Number of radars | Two radars will be available at the time of installation (Malé and Addu), and extension shall be possible up to a total number of 6 radars. |
| CDP-03 | Mosaic space resolution | 1 km by 1 km, adjustable up to 6 km by 6 km. |
| CDP-04 | Mosaicking methodology | Highest observed radar reflectivity or rain rate in the cell. |
| CDP-05 | Time interval between successive mosaics | Adjustable, between 5 and 30 minutes. |
| CDP-06 | Composite picture latency | Less than 5 seconds after arrival of all the radar data. |
| CDP-07 | Precipitation intensity and totals products | Rainfall estimates to take into account the real time AWS precipitation data available in MESSIR NEO for improving the precipitation estimates of the radar mosaic. |
| CDP-08 | Observation data produced | - Maximum observed reflectivity within each cell - Precipitation intensity and local precipitation totals - Reflectivity threshold warning - Doppler velocity threshold warning. - Wind shear and spectrum width threshold warning. - Instantaneous rain rate (mm/h) and 1 – hour accumulation (mm) composites. - VAD wind profiles as applicable. - Quality controlled data for NWP assimilation. |
| CDP-09 | Data overlays | At the forecasters request, overlays shall be available with: - Feng Shui weather satellite information from the CMA receiving station installed in Malé - Meteosat Indian Ocean images, as available - Suitable weather prediction models available in Malé - Wind speed and direction, pressure, temperature and humidity observations from the surface observation network - GIS maps from Google and Open Street |
| CDP-10 | Radar based nowcasting of precipitation cells | Nowcasting of precipitation cells up to 2 hours ahead shall be proposed, based on methods used operationally in at least one other NMS. This will include: - Time lapse presentation of the predicted images, in terms of reflectivity and of rain rate - Estimation on any point of the image domain of the predicted precipitation profile expected for the 2 next hours |
| CDP-11 | Warnings | The contractor is requested to set up an alert production system on MESSIR NEO, with the following main characteristics: - Management of meteorological alerts in the event of severe phenomena. - Selection of the type of phenomenon - Definition of alert levels (according to the color code: green, yellow, orange, red). - Regular monitoring in the event of orange or red alerts. - Automatic dissemination of early warning messages (reports and vigilance maps) to predefined recipients (authorities, media, Civil Security, public) in suitable formats (fax, email, etc.), including the WMO/UNDRR/ITU Common Alerting Protocol (CAP). |
| CDP-12 | Floods warnings | The system must allow early warnings against floods. To do this, the system must allow existing rain observation data and rain forecasts to be viewed on the same interface. This information can then be assembled into alert products. |
| CDP-13 | Wind warnings | The system must allow strong wind detection and forecast (squall line, gust front). To do this, the system will allow existing surface wind observation data to be viewed in order to characterize current risks as well as wind forecasts. This information can then be assembled into alert products. |
| CDP-14 | Warnings at sea | The system will have to make it possible to forecast risks at sea. To do this, the system will have to integrate forecasts on future navigation conditions (height and direction of swell, strength and direction of wind, etc.) which can be adapted according to the type of use at sea. |
| CDP-15 | Users’ interface | This production system should make it possible to provide specific products for different economic sectors, particularly for agriculture, the marine sector (fishing, transport), health, etc.) and the public. This system should enable the automation of production as well as the dissemination of meteorological products to subscribers as well as to the MMS website and mobile application. |

#### Monitoring and maintenance (MMT)

MMT-01	The Contractor shall establish all appropriate measures against system failure.

MMT-02	A fully documented maintenance system with proper document control shall be provided.

MMT-03 	The Contractor shall provide a Maintenance Plan for the entire System, including a schedule for the replacement of parts and overhauls.

MMT-04	The contractor shall provide the maintenance equipment, spare parts, consumables and manuals as defined in MMT-05 to MMT-52.

Table 10: Requested maintenance equipment, spare parts, consumables and manuals

| Purpose | Sec. Nr | Equipment | Number |
| --- | --- | --- | --- |
| SYSTEM MAINTENANCE EQUIPMENT | MMT-05 | Test horn device | 1 |
|  | MMT-06 | Spectrum analyzer | 1 |
|  | MMT-07 | Test signal generator | 1 |
|  | MMT-08 | Power meter | 1 |
|  | MMT-09 | Power sensor | 1 |
|  | MMT-10 | Frequency counter | 1 |
|  | MMT-11 | Detector | 1 |
|  | MMT-12 | Attenuator set | 1 |
|  | MMT-13 | Terminator for Detector | 1 |
|  | MMT-14 | MHz Oscilloscope | 1 |
|  | MMT-15 | Digital Multimeter | 1 |
|  | MMT-16 | High voltage probe |  |
|  | MMT-17 | Diode detector and 3 dB attenuator for pulse width measurements | 1 |
|  | MMT-18 | Portable Power Supply Unit | 1 |
|  | MMT-19 | Network Camera | 1 |
|  | MMT-20 | Tool Kit | 1 |
|  | MMT-21 | Microwave components, including loads, couplers, attenuators, connectors, cables, adapters, etc. | 1 |
|  | MMT-22 | Extension cables | 1 |
|  | MMT-23 | Leveler | 1 |
|  | MMT-24 | Step Ladder | 1 |
|  | MMT-25 | Clump Current Meter | 1 |
|  | MMT-26 | Vacuum Cleaner | 3 |
|  | MMT-27 | Laptop computer, with Intel Core i7 gen 13 processor, 16 GB core memory and 1 TB SSD disk for handling test and repair functions. | 2 |
|  | MMT-28 | Color printer, Inkjet type A3, with 1,200 dpi resolution, 7 pictures per minute printing speed, with LAN Interface. | 1 |
|  | MMT-29 | Basic mechanical equipment and tools for antenna and power generator maintenance. | 1 |
| SPARE PARTS | MMT-30 | Azimuth antenna drive timing belt | 1 |
|  | MMT-31 | Elevation antenna drive timing belt | 1 |
|  | MMT-32 | Azimuth antenna angle encoder | 1 |
|  | MMT-33 | Elevation antenna angle encoder | 1 |
|  | MMT-34 | Motor for azimuth antenna drive | 1 |
|  | MMT-35 | Motor for elevation antenna drive | 1 |
|  | MMT-36 | Servo unit for antenna azimuth drive controller | 1 |
|  | MMT-37 | Servo unit for antenna elevation drive controller | 1 |
|  | MMT-38 | Power supply unit for antenna controller | 1 |
|  | MMT-39 | Power supply unit for transmitter | 1 |
|  | MMT-40 | Power supply unit for digital receiver and signal processor | 1 |
|  | MMT-41 | Magnetron (or solid-state transmitter in case of pulse compression system) | 1 |
|  | MMT-42 | Fan units for radar equipment | 2 |
|  | MMT-43 | LAN Arrester | 2 |
|  | MMT-44 | Stabilized local oscillator (STALO) | 2 |
|  | MMT-45 | Obstruction light | 2 |
|  | MMT-46 | Modulator | 1 |
| CONSUMABLES | MMT-47 | Grease pump and oil with jug for antenna lubrication | 1 |
|  | MMT-48 | Antenna carbon brush for power | 2 |
|  | MMT-49 | Antenna carbon brush for signal | 1 |
|  | MMT-50 | Service manual | 1 |
| Service manuals | MMT-51 | Radar Operation and maintenance handbook | 2 |
|  | MMT-52 | Control and Display Workstation Operation and Maintenance Handbook | 6 |
|  | MMT-53 | Radar Nowcasting MESSIR-NEO Operation and Maintenance Handbook | 3 |

MMT-53 Maintenance contract: The bidders shall submit a detailed Maintenance Contract for the Radar system, encompassing:

- the Defect Liability Period of 540 days from the Date of Completion of Facilities,

- the Extended Defect Liability Period of 5 years from the Date of Completion of Facilities for the radar building water imperviousness, the power supply equipment and the radar transmitter,

- maintenance support, commencing from the Date of Completion of Facilities, to be signed for a period of 10 years, and renewed annually based on satisfactory performance. When not already covered by the ADB standard provisions regarding the Defect Liability Periods, the proposed Maintenance Support shall include the following provisions and conditions:

- The maintenance contract shall cover all equipment and software installed by the Contractor.

- The maintenance contract shall include preventive and corrective maintenance, and free replacement of all types of defective parts/devices and consumables including oil lubrication.

- The removed/replaced defective material becomes the property of the Contractor.

- The Contractor shall provide the details of its call center meant for booking the complaints along with the contact numbers like mobile numbers, phone numbers, mail- address and names etc. of its service engineers.

- The Contractor’s engineers attending to the system are required to make all entries of their work done and corrective measures taken by them with their signatures in the log book kept with the Radar system.

- The radar shall be decommissioned for a period of two weeks for annual-preventive maintenance.

- Yearly uptime of the radar system shall be better than 98% on a yearly base, excluding the 2 weeks of preventive maintenance. If there is a failure of the system for more time than the criterion stipulated here, a penalty will be applicable at the rate of 0.5 % of the yearly cost of the maintenance contract per day exceeding that criterion. The maintenance contract period will be extended by the time the system was under failure and no payment for the extended period for Maintenance Contract will be paid to the contractor.

- If the total failure duration (continuous or intermittent) extends beyond one month, the contract may be terminated at the discretion of the Employer, and the costs of its repair from alternate sources will be recovered from the Contractor.

- Radar down time due to external factors and severe natural calamity beyond human control shall exempt the penalty criteria as in clause above.

- The Contractor will assist MMS for regular backups of all the software.

- The Contractor is required to restore the existing Software from the Backups whenever required.

- The Contractor will be responsible for configuring the networking components.

- If required, the contract may be extended by the Employer. However, the Employer reserves the right to terminate the contract at any time by giving three months of notice, if the performance of the system or the services rendered by the Contractor is not found satisfactory.

#### Training (TRN)

Table 11: Requested training activities

| Spec. Nr. | Course | Topics | Location | Number of trainees | Duration (days) |
| --- | --- | --- | --- | --- | --- |
| TRN-01 | Doppler Weather Radar technology | Power Unit Antenna Radar Unit Meteorological Radar Transmission Unit Computer Network Unit Power Back-up Unit Application Software | Addu | 6 IT | 5 |
| TRN-02 | Factory training | System design, operation, maintenance, calibration and fault identification of the radar system along with modification & up-gradation in application software | Factory | 2 IT 2 managers | 10 |
| TRN-03 | Radar control and display workstations maintenance | Power Unit Computer Network Unit Application Software | Addu | 6 IT | 5 |
| TRN-04 | Radar mosaicking and nowcasting system maintenance and development | Power Unit Computer Network Unit Application Software | Malé | 4 IT | 5 |
| TRN-05 | On the job DWR observation and nowcasting techniques | Fundamentals of Radar meteorology Radar image interpretation Nowcasting case studies | Malé | 6 forecasters | 10 |
| TRN-06 | On the job maintenance training | Inspection, adjustment, minor fault finding, remedy and recovery, and major fault countermeasures: (1) routine maintenance using measuring instruments and tools, (2) practice of replacing spare parts into the actual system and the subsequent confirmation of system operation, (3) practice of remedy, recovery and major fault countermeasures, distributing information to the manufacturer and receiving technical advice) | Addu | 4 IT | 5 |
| TRN-07 | Managers training in radar meteorology, focused on operations and maintenance. | a) introduction to weather radar principles and technology, b) operating principles of weather radars, c) preventive and corrective maintenance of electronic equipment, d) calibration and verification of radar performance, e) diagnosis and fixing of problems, f) electrical safety and safety at work. | In a NMS with a strong DWR experience to be proposed by the Contractor | 1 manager | 20 |
| TRN-08 | Managers training in radar meteorology, focused on operations and data interpretation. | a) introduction to weather radar principles and technology, b) operating principles of weather radars, c) DWR data processing, d) DWR data interpretation, d) DWR radar mosaicking and nowcasting techniques. | In a NMS with a strong DWR experience to be proposed by the Contractor | 1 manager | 20 |

For all the above-mentioned trainings, the following minimum requirements must be ensured:

(i) Attendance sheet, disaggregated by sex (male/female)
(ii) Training schedule, including allocated time, facilitators, and session details
(iii) Pre-test and post-test assessments
(iv) Detailed training report, covering topics delivered, key observations and recommendations, evaluation results (both technical content and training facilities/resources), and relevant photographs

#### Project signage requirements

GEN-18: The Contractor is responsible for the design, supply and installation of the project information signage. The signage shall provide relevant information to the public about the project, including the proper designation of the project, the Employer, the Contractor and the Bank.

GEN-19: For this purpose, sign boards shall be installed at the Site as soon as practicable after the Commencement Date and shall remain in place at all times until Completion of the Facilities. If sign board(s) is(are) damaged or becomes unreadable during this period, it shall be promptly replaced by the Contractor at the Contractor’s cost.

GEN-20: The sign board design shall be submitted by the Contractor to the Project Manager for approval in accordance with Sub-Clause 20.3 [Approval/Review of Technical Documents by Project Manager]. Unless otherwise required under the applicable Laws, the sign board design should comply with the following:

- General

- One sign board at the entrance of the construction site on Addu, the precise location to be determined in consultation with the Project Manager.

- Content

- Maldives flag/logo

- Project and Contract title

- Accepted Contract Amount

- Time for Completion

- Bank’s name and logo (in accordance with Branding Tool Kit – Visual Identity guidelines of the Asian Development Bank and, as the case may be, other financiers’ requirements)

- Employer’s name

- Contractor’s name

- Project Manager’s name

- Complaint handling contact information (email and/ or phone number)

- Design

- The General layout including sample colors: to be proposed by the Contractor

- Dimensions: minimum of 2.5 m x 2.5 m

- Font size and type: should be such as to ensure that the content shall be visible from a distance

- Language of the signage: Dhivehi and English

- Material and support:  the sign boards shall be made of a material that shall be weatherproof and installed as appropriate to withstand the whole execution period until taking-over of the Works

GEN-21: No other signage apart from environment, health and safety information and instructions is allowed except with the approval of the Project Manager. The Contractor shall not post, nor display any sign or item that could provide misleading information about the project. No national symbols or flags other than those of the Country may be displayed without the express approval of the Project Manager.

#### Deliverables and delivery schedule

Table 12 shows the list of deliverables and the requested delivery schedule.

Table 12: List of expected deliverables and schedule

| Article Nr. | Specs. class. | Description | Number | Place of acceptance | Destination | Delivery date after contract Effective Date (months) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Earliest | Latest | Proposed by bidder |
|  | GEN | Inception report | 1 | Malé | Malé |  | 1 |  |
|  | GEN | Radar system detailed design study, including the detailed building design | 1 | Malé | Malé |  | 5 |  |
|  | RBG | Radar building delivery | 1 | Addu | Addu |  | 12 |  |
|  | TRN | Training TRN-01 completed | 1 | Addu | Addu | 8 | 12 |  |
|  | TRN | Training TRN-02 completed | 1 | Factory | Factory | 6 | 12 |  |
|  | DWR | Transmitter and receiver unit | 1 | Factory | Addu |  | 12 |  |
|  | DWR | Antenna and radar control unit | 1 | Factory | Addu |  | 12 |  |
|  | DWR | Signal processor | 1 | Factory | Addu |  | 12 |  |
|  | DWR | Radome, antenna and pedestal | 1 | Addu | Addu |  | 15 |  |
|  | TRN | Trainings TRN-03, TRN-04, TRN-07 and TRN-08 completed | 1 | Addu | Addu, Malé | 15 | 20 |  |
|  | CDS DTR | Control and Display workstations | 3 | Addu, Malé | Addu, Malé |  | 20 |  |
|  | CDP DTR | MESSIR NEO interface and software | 1 | Malé | Malé |  | 15 |  |
|  | All | Operating and application software | 1 | Malé | Addu, Malé |  | 20 |  |
|  | TRN | Training TRN-05 completed | 1 | Malé | Malé | 20 | 24 |  |
|  | All | Site acceptance of any not listed above item | 1 | Addu | Addu, Malé |  | 24 |  |
|  | All | Installation | 1 | Addu, Malé | Addu, Malé |  | 20 |  |
|  | All | Documentation | 1 | Malé |  |  | 24 |  |
|  | MMT | Monitoring and maintenance equipment sets along with all accessories required for complete set-up for testing and measuring radar parameters. | 1 | Addu | Addu, Malé |  | 20 |  |
|  | TRN | TRN-06 completed | 8 | Maldives, factory, foreign NMS | N.A. | 20 | 24 |  |
|  | MMT | Time for completion, commissioning, guarantee tests and operational acceptance | 1 | Addu, Malé | N.A. |  | 24 |  |
|  | MMT | Defect Liability Period | 1 |  |  |  | 42 |  |
|  | MMT | Extended Defect Liability Period applicable to: - Radar building roof - Power supply equipment - Radar transmitter | 1 |  |  |  | 84 |  |
|  | MMT | Maintenance period | 1 |  |  |  | 144 |  |

### Environmental, Health and Safety Management Requirement

- Anticipated Environmental Impacts

- Construction Phase

- Impacts on the Physical Environment

Air: the Addu radar will be in a remote location with good air quality. Some dust may be generated by construction and fabricated material transportation traffic and excavation work, which is predicted to be low with no significant impact outside the immediate vicinity of the worksite. Standard controls are (i) use of equipment in good condition; (ii) correct engine maintenance; (iii) contract provisions allowing the Employer to ban vehicles emitting black smoke; (iv) routine testing of air quality and dust (PM10 and PM2.5) near sensitive receptors, if any (old mosque and cemetery); and (v) effective community liaison and grievance procedures, so that polluting vehicles can be reported, identified and sanctioned; (vi) spray water on exposed work area and aggregate stockpile; (vii) cover the tippers transporting construction material.

Noise: the radar system project site at Addu International Airport is subject to aircraft noise. Background levels will be established at the start of construction. Noise will be generated by all construction vehicles and by some stationary construction equipment such as generators and cement mixers. Standard controls are (i) use of effective silencers on all vehicles and machinery; (ii) contract provisions allowing the Employer to ban machinery causing noise well above WHO standards; and (iii) effective community liaison and grievance procedures, so that excessively noisy vehicles and equipment can be reported, identified and sanctioned. There are no sensitive receptors around the area except an old mosque and a cemetery near the project site.

Vibration: the civil works will not involve vibration-inducing activities such as blasting or pile-driving. The only source of vibration foreseen is, possibly, vibro-compaction of base layers for the access road for the Addu radar. If any structures close to roads used by construction traffic are considered fragile, a condition survey should be carried out as early as possible. If any problem occurs or is perceived, it can be reported and followed up through the standard measure of an effective community liaison and grievance procedure.

Surface water and groundwater: work on the Addu radar system will not affect surface water because this does not exist in the planned location. Appropriate surface drainage management will be provided along the various short lengths of paved roads required to service this facility. Leakage of fuel and chemicals on ground shall be avoided by applying control and appropriate disposal measures. No impacts on groundwater are anticipated from implementation of the work.

Soil, erosion and sedimentation: all the construction works are small scale and will take place essentially on flat surfaces. There is no possibility of erosion in the form of gullying. However, if heavy rain falls on excavated surfaces such as trench for foundation, there may be a small overflow of sediment-laden runoff. Any such impact will be very short-term and localized. Mitigation includes sequencing works so as to minimize the area of ground exposed and constructing silt-traps at the lower edge of work sites so as to detain runoff and promote settlement.

Site access: all the construction sites are accessible from existing paved roads, subject to airport security clearances.

Existing services: Local consultations and fieldwork have identified various services that might be affected by the works. The existence and exact locations of all services will be checked during detailed design through coordination with service providers. Any temporary disruption should be minimized.

Construction materials: the radar system will have very small requirements for bulk construction materials.

Waste management, pollution and site housekeeping: all construction operations generate a variety of solid and liquid wastes, ranging from inert substances such as rubble and bricks through wood waste from formwork, plastics, metal in various forms, workshop wastes, wastewater from worker accommodation, staff offices and site sanitation, office waste, and kitchen wastes if there are canteens. For the project, the most important category of waste will be used engine oils and filters from vehicle maintenance, because these have the potential to create both soil and water contamination. The physical works are not expected to generate any other wastes in any significant quantities. Waste management, pollution prevention and site housekeeping will be ensured by standard provisions and to the satisfaction of the PIU. This will require the contractor to develop and implement a site waste management plan. This will cover identification of all waste types; separation of all wastes into different waste streams; collection and storage of wastes; disposal of all wastes by approved methods in the hierarchy re-use, recycle, safe disposal; record keeping; specific requirements in relation bulk fuel storage and vehicle maintenance, including by subcontractors on the site; emergency response in case of spills or soil contamination; arrangement with the local government for collecting the waste under their regular waste management system, and awareness and training to workers.

- Impacts on the Biological Environment

No important ecological habitats or environmentally sensitive areas have been identified in the vicinity of the location for the Addu radar system.

- Impacts on the Social Environment

Airport safety: the radar system will be located within the perimeter of an active airport. The Contractor will need to liaise with the Employer and the airport management authorities to obtain security clearances for all staff, workers and vehicles. The Contractor will also be required to attend a site-specific briefing by the respective airport authorities in relation to safety and security.

Construction traffic and disturbance: construction of the Addu radar system and rehabilitation is not expected to result in any significant negative impact from construction traffic since the scale of the works are small and there will only be a limited number of vehicle movements. Nevertheless, required informative signboard informing the on-going work and any diversion requirement shall be placed at required location to inform the public.

Public health: apart from possible road traffic accidents, no impacts on public health are foreseen from the project activities. There may be some interaction between local residents and the contractors’ staff and workers, but the number of workers will be small and Maldives are socially conservative and alcohol-free. Prevention of STD transmission is a public health issue, and will be managed as a specific item in the contractor’s induction health, safety and environment training for all staff and workers.

Occupational health and safety (OHS): all construction work may cause health and safety risks. The project works are relatively simple although they will involve working at a height, in confined spaces, with electricity, and with heavy machinery. There will also be the usual minor risks associated with vehicle maintenance and small-scale construction work. All these risks can be mitigated by standard mitigation measures suggested by EMP, including (i) using equipment in good condition, and properly maintaining it; (ii) ensuring all equipment operators are fully qualified, and also experienced; (iii) including a full range of health and safety requirements in the tender documents, including the need for at least one site engineer to have health and safety qualifications; first aid equipment and a minimum number of qualified first aiders amongst site workers; risk assessment procedures; and procedures in case of accidents; (iv) a requirement for the contractor to develop and implement a health and safety plan (including community health and safety); (v) ensuring that the contractor provides health insurance for all staff and workers as well as complying with relevant Maldivian regulations on worker health and safety; and (vi) including OHS expertise in the PIC.

Land, compensation and resettlement: no land acquisition or resettlement is currently foreseen. Activities will be undertaken on Government-owned land.

Heritage: Gan has an old mosque and cemetery as cultural heritage near the proposed radar tower site. This must be protected from all construction activities and disturbance from noise and air pollution.

- Operational phase

Operation of the new and rehabilitated radar domes will not involve any unusual activities beyond the normal requirements for maintenance of sensitive electro-mechanical equipment and protection of the structures in tropical coastal environments characterized by salt spray, frequent rain and occasional high winds. Any electronic components and used batteries will be returned to the suppliers for recycling until such time as appropriate recycling facilities become available, and in all cases handled and disposed of in compliance with the Waste Management Policy and Regulations (2013) of Maldives.

- Environmental Safeguards Clauses in the Construction Contract

  - SSEMP

Within 28 days from the date of the Letter of Acceptance and prior to field mobilization, the Contractor shall submit a detailed Site-Specific Environmental Management Plan (SSEMP), including final health and safety plan (H&S Plan) and other plans as required for the Project Manager’s no objection showing how it intends to comply with environmental, health and safety laws and regulations and other specific requirements prescribed in the Contract. The plans shall address all the monitoring and mitigation measures set forth in the final or updated Environmental Management Plan (“EMP”) of the project as well as related Supplementary Information attached in Section 6 - Employer’s Requirements in the bidding document.

The following environmental provisions will be included and operationalized in the Site-Specific Environmental Management Plan (SSEMP) to be produced by the successful bidder to provide the required construction-phase mitigation and monitoring measures.

  - Commencement

The Contractor shall not commence any “Physical Works” including site establishment and tree or vegetation clearance until (i) written confirmation is received from the Employer, (ii) the Contractor has obtained all required environment; health and safety (labor) permits or licenses, (iii) the Contractor has undertaken and reported to the Employer on the findings of all applicable pre-construction environmental survey work and baseline environmental monitoring requirements as set out in the definitive version of the EMP, (iv) the Contractor has incorporated all the applicable requirements of the definitive version of the EMP into their detailed designs; (v) the Contractor has submitted the detailed designs and all environmental, health and safety sub-plans required by the definitive version of the EMP and received written confirmation from the Employer of their approval. Such confirmation of no objection by the Project Manager shall not relieve the Contractor of any of his/her obligations or responsibilities under the Contract.

  - Staff

  - EHS Officer

The Contractor shall appoint at least one fulltime qualified and experienced Environment; Health and Safety Officer (“EHS Officer”) to supervise and monitor SSEMP and health and safety plan implementation on a day-to-day basis for the duration of “Physical Works” under the contract and also act as a grievance redress mechanism focal point to keep affected persons informed of works and be available to receive, document, and deal with any grievances at the project site level.

  - EHS awareness and training

The Contractor shall ensure that all its design and construction staff, as well as the staff of subcontractors and third parties employed by them, regardless of whether they are formally or informally contracted, understand their responsibilities to implement the SSEMP with appropriate environment; health and safety (EHS) training being provided by the Contractor including construction-site EHS inductions, emergency procedure drills, monthly refresher trainings, and daily toolbox talks. The Contractor shall ensure all construction staff, including the staff of subcontractors and third-parties employed by them, have attended the necessary specialized, task-specific training and are medically fit to perform their role.

  - Forced and child labor

The Contractor will ensure no forced or child labor or persons under 18 are employed on the project. They will also ensure that child labor is not used by the supplier of material and equipment to the project.

  - Labor welfare

The Contractor is to ensure sufficient sanitation and welfare facilities (with all wastewater discharges connected to a sewerage system or bio septic tank with soakaway or self-contained portable bio-toilets) are available at each construction site and at any worker camps or accommodation provided by them or their subcontractors with a ratio of at least 1 toilet per every 6 persons. Open defecation and urination shall beprohibited. Use of pit latrines shall also be prohibited, and no direct discharge of untreated wastewater to surface water or groundwater is allowed.

The contractor is to ensure worker camps or accommodation provided by them or their subcontractors complies with all national and state requirements as well as the ILO guidelines on worker accommodation. No such accommodation will be permitted at the worksites or within the airport perimeters, except for the services for any necessary overnight security personnel. Use of old and rusted iron sheet, tarpaulin and plastic shall not be permitted to use in camp construction, and the camp shall comply with the standard mentioned in the EMP and the contract.

If a local water source is to be used as drinking water supply it must be licensed for abstraction and be subject to adequate treatment to enable WHO drinking water standards to be maintained, the quality of raw and treated water to be tested regularly to confirm drinking water standards are met.

  - Environmental Protection and Control of Pollution

- General

The Contractor shall observe and comply with all National Laws, Government Regulations, and Presidential Decrees.

- Materials

The Contractor will ensure no CFCs, no PCBs and no asbestos-containing materials are used in the project. Any transformers purchased shall be accompanied by a letter from the manufacturer stating that they are guaranteed PCB-free and labelled as PCB-free before installation. Other materials and equipment purchased shall be accompanied by a letter from the supplier or manufacturer saying they are guaranteed asbestos-free.

Sand and gravel will only be obtained from existing approved sources with environmental clearance and all sources of water for construction will have an abstraction license. Records will be kept of the volume of all materials used and their source.

- Waste

As part of the SSEMP, the Contractor shall establish and implement a waste management plan based on the principles of reduction, re-use, recycling and safe disposal in accordance with the requirements of the Employer and national regulations. Waste shall be collected and separated on site for recycling or disposal recycling through reputable, legitimate, licensed third parties and/or to suitably licensed and engineered waste management facilities. The Contractor shall keep a record of waste volumes and disposal pathways for monthly reporting including the relevant permits and/or waste destruction certificates.

- Pollution of watercourses

The emission of polluting liquids or other waste into drains, water courses, or groundwater shall not be permitted.

No concrete or cement washings from the works or drainage from the Contractor's concrete batching and mixing areas, asphalt (hot mix) plants, or other manufacturing or production facilities shall be allowed to discharge into streams or drains without passing through an adequate system of settling ponds.

Storage of fuels, fueling and maintenance of plant and vehicles, etc. shall take place only on sites and under conditions that do not allow spilt fuels to be discharged to water bodies. Fuel storage and fueling areas shall be equipped with adequate protective measures to confine and retain accidental spillages. No drainage from fuel store and plant maintenance depots shall be allowed to be discharged without passing through an adequate arrangement of oil traps and separators.

Spill prevention kits (sorbent pads for spill, absorbent material, etc.) shall be available at storage areas and other at-risk locations within clearly labelled containers. Worker managing spill shall use full protective gear including gloves, goggles and boot.

Washing of vehicles shall only be done in specially designated and equipped areas with drainage and collection chamber around the site.

Adequate sanitary waste control facilities shall be provided in site offices and workers camps, and sewage waste shall be collected regularly and disposed in accordance with relevant environmental legislation.

The Contractor shall accordingly be responsible for the installation, operation and maintenance of a comprehensive surface drainage system to all areas of the Works. The system shall be constructed such that no discharges of oil, cement, silt or other liquid or solid waste matter can enter the streams and water courses at the site; and it shall have all necessary solid waste and sediment traps, settling ponds, oil separators, etc., required to ensure that pollution of the soil and marine environment does not occur. The Contractor shall be responsible for maintaining the system to the satisfaction of the Employer’s Construction Supervisor and all costs of providing the system shall be deemed to be included in the various rates and lump sum items for the works included in the priced Bill of Quantities.

- Air pollution

The Contractor shall take all necessary steps to minimize air pollution resulting from his/her operations.

Except where stipulated in the Specifications for the disposal of natural vegetation and organic materials from clearing operations, the burning of waste materials for disposal, particularly oil and petroleum wastes, rubber, plastics and similar materials will not be permitted.

During the performance of the work required under the Contract or of any operations appurtenant thereto, whether on the Project Site or elsewhere, the Contractor shall take all steps necessary, and shall furnish all labor, equipment, materials and means, required to reduce dust nuisance from the Works, and to prevent dust originating from his/her operations from damaging crops, orchards, cultivated fields, and dwellings; or causing a nuisance to persons. The Contractor shall be held liable for any damage resulting from dust originating from his/her operations including on Government roads, rights-of-way or elsewhere.

The emission of dust into the atmosphere shall not be permitted during the manufacture, handling and storage and handling of cement and of concrete aggregates, and the Contractor shall use such methods and equipment as are necessary for the prevention, or the collection and disposal, of dust during such operations. All truckloads of loose materials shall be covered during transportation.

Emission outlets shall be fitted with pollution control devices in compliance with relevant current Government emission control legislation.

The cost of spraying water on haul roads, access roads, government roads, aggregate stockpiles, etc.; or of any other methods of reducing the formation of dust; and the cost of furnishing and applying materials to maintain the works areas, adjacent areas, and roads, in a dustless condition, shall be deemed to be included in the various rates and lump sum items for the works included in the priced Bill of Quantities.

- Noise pollution

The Contractor shall take all necessary precautions to minimize the amount of noise and vibrations coming from construction activities.

The Contractor shall ensure that all plant and equipment is properly maintained in good operating condition, and that noisy construction activities shall be effectively reduce sound by means of silencers, mufflers, acoustic linings or shields, acoustic sheds or screens or other means, to avoid disturbance to any nearby noise sensitive receivers, as is required. All plant and equipment shall comply with relevant Government legislation covering sound emissions.

Operation of trucks and heavy vehicles and machinery shall be restricted to the hours of 06:00 to 21:00.

All necessary measures shall be undertaken to protect schools, hospitals and other adjacent noise sensitive receptors, including the use of noise barriers.

- Damage to property, crops, and vegetation

The Contractor shall limit the movement of his/her employees and equipment within the project area and on adjacent land, including access routes approved by the Employer’s Construction Supervisor, so as to minimize damage to natural vegetation, crops and property, and shall endeavor to avoid any damage to land.

The Contractor shall strictly ensure employees and equipment do not enter any sensitive environmental areas that are demarcated as “no-entry” zones.

The Contractor shall preserve existing trees, plants and other vegetation that are to remain within or adjacent to the Works and shall use every precaution necessary to prevent damage or injury thereto. Trees or shrubs shall only be felled or removed where such impinge directly on the permanent works or necessary temporary works areas; and where such is approved by the Employer’s Construction Supervisor.

On completion of the Works all areas disturbed by the Contractor’s construction activities shall be restored by the Contractor to their original condition, or as may be acceptable to the Employer.

The Contractor shall be responsible directly to the Employer for any excessive or unnecessary damage to crops or lands arising from his/her operations, whether within the project area, on lands adjacent thereto, or adjacent to approved access roads: and deductions will be made from the payment due to the Contractor to cover the cost of such excessive or unnecessary damage, as determined by the Employer.

- Chance finds

In case of a chance find of any potential cultural heritage artefact the Contractor will stop work at that location and immediately inform the Employer to determine the appropriate course of action.

  - Health and Safety

- General

The Contractor shall undertake a health and safety risk assessment and as part of the SSEMP and OHS Plan and shall develop a Health and Safety Plan, incorporating emergency preparedness and response plans for approval of the Employer. The Contractor shall take all measures and precautions necessary to ensure the health, safety and welfare of all persons entitled to be on the site and will ensure that works are carried out in a safe and efficient manner. Such precautions shall include those that, in the opinion of the Employer, are reasonable to prevent unauthorized entry upon the site and to protect members of the public from any activities under the control of the contractor.

- Site supervision

The Contractor will ensure that if multiple sites are operated each active construction site has adequate health and safety supervision to ensure the health and safety of all workers and local communities. This is to include a suitably qualified and experienced Health and Safety Supervisor who is fulltime present at the active construction site.

- Personal Protective Equipment

The Contractor shall ensure that its construction staff, as well as the staff of subcontractors and third parties employed by them, regardless of whether they are formally or informally contracted, are provided with and wear at all times when they on the construction site adequate Personal Protective Equipment appropriate to their role. This will include but not be limited to safety helmets, gloves, safety boots, goggles and other eye protectors, hearing protectors, and safety harnesses when working at height.

- First aid

The Contractor shall provide and maintain a suitably equipped and accessible first aid station at each of the radar installations when work is in progress. First-aid kits shall contain an adequate supply of unexpired sterilized dressings and bandages with other necessary first aid equipment as per national health and safety (labor) laws and regulations and the EMP requirements, including emergency eyewash facilities. First aid kits shall also be carried by all vehicles used by the Contractor and any subcontractors for the Works.

Free access for workers to a qualified nurse and/or doctor must be provided in relation to any work-related incident.

The Contractor shall ensure that at least one qualified First-Aider is present on each work site at all times when work is in progress. This person shall be responsible for maintaining the first aid kits and initiating any emergency response to incidents involving injury, in line with the approved emergency response plan in the Health and Safety Plan.

- Worksite sanitation and welfare

Adequate sanitation and welfare facilities for all staff and workers shall be provided at each construction site, including toilets and washrooms with hot and cold running water and soap, a drinking water supply meeting WHO drinking water standards, a rest/eating area with fan, table and chair, and a prayer facility.

- Communicable diseases

The Contractor shall be required to comply with national restrictions for containing the spread of communicable diseases, if any. If any pandemic is declared by WHO, the Contractor shall undertake a pandemic specific health and safety risk assessment and as part of the Health and Safety Plan shall prepare a management plan following national guidance and WHO recommendations. The Contractor shall also carry out communicable disease awareness programs for labor, disseminate information at worksites on the risks of the pandemic and other communicable viral diseases, and provide adequate handwashing facilities and personal protective equipment, as part of health and safety measures for those employed during construction. The contractor shall keep in stock a few ready-made tent to use as quarantine in case of need.

- Fire

The Contractor shall provide and maintain all necessary temporary fire protection and firefighting facilities during the construction of the Works and shall comply with all national fire safety requirements. These facilities must include in-date, serviced, portable fire extinguishers suitable for fighting the potential hazards on the construction site and in all vehicles used by the Contractor and any subcontractors for the Works.

- Grievance redress mechanism

The Contractor shall ensure that throughout the period of the physical works signage is prominently visible for local communities and workers detailing the contact points and focal persons for the Contractor and Employer. Also disseminated shall be the Grievance Redress Mechanism established in the project.

  - Reporting

The Contractor shall establish an operational system for managing and monitoring environmental, health and safety impacts and risks, progress with implementation, and compliance with SSEMP, EMP and OHS requirements. The Contractor’s management and EHS staff will attend monthly progress meetings convened by the Employer at which EHS will be an agenda. They will prepare monthly reports on EMP/OHS status and compliance as a section in the monthly and quarterly progress reports documenting mitigation measures and monitoring activities carried out, issues encountered including all environmental incidents, near misses and accidents, grievances received, and follow-up actions that were taken (or will be taken) to correct issues.

The Contractor shall maintain a record of all emissions and spills of liquid, solid and gaseous matter which occur at the site, whether into water courses, streams, on land, or into the air. This record shall be compiled daily and shall include details of date, time and nature of the event, along with details of the remedial and clean-up measures carried out. Copies of these records shall be given to the Employer on monthly basis.

The Contractor shall also maintain a record of any complaints made by any Governmental or Community Organization or by the public, regarding his/her operations. This record shall contain the date and time of receipt of the complaint, the name and address of the complainant and the action taken to remedy the situation. Copies of these records shall be given to the Employer on monthly basis

  - Environmental Management Plan

The Contractor shall observe and comply with all relevant environmental protection and mitigation, monitoring, and reporting requirements stipulated in the Environmental Management Plan (EMP) and in the Particular Conditions of Contract. In the event of any conflict between the foregoing sub-clauses and the environmental protection and mitigation measures and pollution control requirements of the EMP, the EMP shall take precedence.

The Contractor shall prepare and submit to the Employer’s Construction Supervisor a SSEMP demonstrating the manner in which the Contractor will comply with the requirements of the foregoing subclauses on Environmental Protection and Pollution Control, the EMP, and any particular environmental mitigation measures as stipulated in the Particular Conditions or Technical Specifications forming part of the Contract Documents.

The SSEMP shall be submitted within 28 working days of the Contractor receiving the Notice to Proceed with the Works, and shall include the set of management plan listed as part of the EMP (e.g. waste management plan, dust management plan, noise management plan, surface water management plan, emergency management plan, health and safety management plan, or any other management plan as stated in the EMP). Training shall be provided to workers about the appropriate implementation of the SSEMP. Contractor shall not mobilize in the field and construction or rehabilitation works shall not start until the SSEMP is approved by the EA.

  - Payment

Payment for compliance with the EHS provisions of the contract will be made in accordance with the Unit Rates, Lump Sum or Provisional Sum Items included in the Priced Bill of Quantities. Except where otherwise agreed or provided for by the Employer, no other payment will be made for complying with the EHS provisions of the contract. All costs shall be deemed to be included in the prices for the Contractor’s mobilization for construction, and the various rates and lump sum items for the works included in the priced Bill of Quantities.

The Employer may withhold payment if monthly reports are not submitted within 15 working days of month end or in the event that corrective actions required by the Employer have not been addressed by the Contractor within 30 days.

### Drawings

Figure 1: Map of Addu City atoll and Project island location

Figure 2: Map of Gan island (Addu City) and location of current MMS office

Figure 3: Proposed new MMS office plot, nearest substation and location of Addu Radar

Source: Approved Site Location.

Table 13 Coordinates of Site Boundary Addu Radar

| P | N | E | Z | Latitude_DD | Longitude_DD | Latitude_DMS | Longitude_DMS |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 9923190 | 293684.9 | 0 | -0.694556989 | 73.14608862 | 0° 41′ 40.41″ S | 73° 8′ 45.92″ E |
| 2 | 9923202 | 293674.9 | 0 | -0.694453063 | 73.14599871 | 0° 41′ 40.03″ S | 73° 8′ 45.60″ E |
| 3 | 9923200 | 293696.4 | 0 | -0.694466477 | 73.14619186 | 0° 41′ 40.08″ S | 73° 8′ 46.29″ E |
| 4 | 9923212 | 293686.3 | 0 | -0.694362914 | 73.14610154 | 0° 41′ 39.71″ S | 73° 8′ 45.97″ E |

### 5.  Supplementary Information

#### Radar building quality control plan

The ambient and concrete temperatures will be measured during concrete pouring to ensure correct concrete quality and concrete pouring work at nighttime when the outside air temperature goes down is required. Table 11 describes the control plan work.

Table 14: Radar building quality control plan

| Work | Work Type | Control Item | Method | Remarks |
| --- | --- | --- | --- | --- |
| Structural Work | Concrete work | Fresh concrete Concrete strength | Slump, air volume, temperature Comprehensive strength test Chloride Quantity Test Alkali Aggregate reactivity Test | Concrete strength test will be conducted at a public test institution. Chloride quantity test and alkali aggregate reactivity test will be conducted by a private laboratory. |
|  | Reinforcing work | Reinforcing bar Arrangement | Tensile test, mill sheet check Bar arrangement check Factory inspection sheet check | Tensile test of reinforcing bar will be conducted by a private laboratory. |
|  | Pile work | Material, bearing capacity | Bearing capacity check |  |
| Finishing work | Roof work | Workmanship, leakage | Visual inspection, water spray test |  |
|  | Tile work | Workmanship | Visual inspection |  |
|  | Plastering work | Workmanship | Visual inspection |  |
|  | Door & Window work | Products, Installation accuracy | Factory inspection sheet check Visual inspection, dimension check |  |
|  | Painting work | Workmanship | Visual inspection |  |
|  | Interior work | Products, workmanship | Visual inspection |  |
| Electrical Work | Power Receiving and Transformer | Performance operation and installation check | Factory inspection sheet check, voltage, power delivery check |  |
|  | Conduit work | Bending, support check | Visual inspection, dimension check |  |
|  | Wiring and cable work | Sheath damage, loose connection check | Performance sheet check, cleaning before laying, marking after bolt fixing |  |
|  | Lightning work | Performance, operation, installation check | Performance sheet check, illumination measurement, visual inspection |  |
| Mechanical work | Water piping work | Support pitch, leakage | Visual inspection, leakage, water pressure test |  |
|  | Pump installation | Slope, support pitch, leakage | Visual inspection, leakage, flow test |  |
|  | Air conditioning work | Performance, operation, installation check | Performance sheet check, temperature measurement |  |

#### Worksite environmental management, safety and good practice

The Contractor shall comply with all applicable national environmental, health and safety (labor) laws and regulations and the labor standards of the International Labor Organization (ILO).

The Contractor shall comply with the Employer’s project financier’s safeguard requirements [ADB’s Safeguard Policy Statement (2009)] and the World Bank Group’s General Environmental, Health and Safety Guidelines and the guidelines on Telecommunications.

#### IEE and EMPs

The Contractor shall implement the mitigation measures and carry out the monitoring requirements assigned to them as set forth in the initial environmental examination (“IEE”) prepared by the Employer in accordance with the project financier’s safeguard requirements [ADB’s Safeguard Policy Statement (2009)] and the environmental management plan (“EMP”) and environmental monitoring plan (“EMonP”) and any subsequent updates to them. Mitigation and monitoring plans extracted from the EMP are attached in Annexes A and B to this section. These may be updated and the EMP to be complied with by the Contractor will be disclosed in the Employer’s and project financier’s [ADB] website. The Contractor shall also implement the mitigation measures and carry out the monitoring requirements assigned to them as set forth in the environmental management plan (“EMP”) prepared for the radar works by the Employer in accordance with the Environmental Protection Agency’s requirements and shall comply with any conditions attached by the Agency to the environmental permit for the works. The EMP prepared under the environmental impact assessment conducted in accordance with the national environmental requirements and legal provisions of the Government of Maldives will be attached as Annex C (when available); and the EPA’s conditions to the approval of EMP will be attached as Annex D (when available]. In case of any inconsistency between the requirements of the two EMPs, the Contractor will follow the Employer’s instructions.

The IEE includes a template for a Site-Specific Environmental Plan (SSEMP), attached at Annex E to this section.

The Contractor shall ensure mitigation measures are implemented at construction sites as well as at the workers camps provided by them or their subcontractors. The Contractor shall allocate required budget and staff required to ensure  that the requirements are met, and implement corrective action plans required by the Employer. The Contractor shall cover the cost of corrective action required in response to non-compliance with the definitive version of the EMPs or property damage caused by the contractor, subcontractors and third parties employed by them.

Annex A: EMP from ADB IEE

| Activity / Topic | Impact | Mitigation Measure | Responsibility |
| --- | --- | --- | --- |
| Planning & Design Phase |  |  |  |
| Impact assessment | If no assessment, potential for significant unmitigated negative impacts | Undertake impact assessment in line with ADB policy and Maldives procedures | PMU |
| Environmental management | If no environmental management plan, identified impacts will not be mitigated | Prepare EMP as part of safeguard documentation Update ADB IEE during detailed design phase PMU Environmental Safeguards Specialist to review updated IEE and submit to ADB for approval Obtain approval to the IEE from the Government of Maldives Include approved, updated IEE, WMP and EPA conditions in the bidding documents Include comprehensive safeguard provisions in the bidding documents | PMU |
| Grievance redress | If no system for submitting and solving complaints, subproject may be delayed and government suffers reputational damage | Design accessible and effective grievance redress mechanism | PMU |
| Heritage site | If not avoided, heritage site on Gan becomes impacted by subproject 1.1 | Heritage site to be avoided and not impacted by the radar tower construction, access to remain open, and structures shall not be affected | PMU |
| Environmental supervision and monitoring | If unclear or under-resourced arrangements for environmental monitoring & supervision, implementation of EMP may be affected | Prepare Environmental Monitoring Plan as part of safeguard documentation | PMU |
| Construction Phase |  |  |  |
| Air quality | Excessive dust from earthworks and construction traffic | Dust suppression by watering at sensitive locations when required Cover loads on trucks during transportation | Contractors |
| Noise | Disturbance to residents | Ensure all equipment have silencer Limit working hours | Contractors |
| Vibration | Damage to structures from passage of heavy trucks | Survey structures close to road considered to be fragile Repair/compensation for any damage occurred from construction work and movement of heavy machineries | Contractors |
| Surface water and sedimentation | Mobilization of sediment from earthworks during rainstorms | Minimize duration of exposed, non-hardened earthworks Silt traps at edge of work sites | Contractors |
|  | Temporary reduced access to facilities on roads | Temporary bypasses will be provided to support traffic flow Public notices will be provided to inform about planned works | Contractors |
| Public roads and bridges | Damage to public roads from heavy construction vehicles | Condition survey prior to start of operations Monitor road conditions Repair any damage or deterioration and keep road at pliable condition at all times | Contractors |
|  | Temporary increased traffic congestion | Temporary bypasses will be provided to support traffic flow Public notices will be provided to inform about planned works and schedule | Contractors |
| Existing services | Damage or cutting of existing services, potentially including sewer pipes, internet cables and other services | Check location of all services before start of any physical works, and integrate measures around existing utilities Reinstate public utilities at the earliest and keep the users informed | PMU / Contractors |
| Construction materials | Supply from unauthorized sources | Ensure all construction materials (aggregates and rock) are sourced from authorized sources and in accordance with the permit conditions, and as approved by PIU | Contractors PIU/PMU |
| Waste management & pollution prevention | Contamination of soil and water by liquid and solid wastes from contractor’s activities | Include standard provisions in the tender documents which will require the contractor to develop and implement a site waste management plan. This will cover identification of all waste types; separation of all wastes into different waste streams; collection and storage of wastes; disposal of all wastes by approved methods in the hierarchy re-use, recycle, safe disposal; record keeping; specific requirements in relation bulk fuel storage and vehicle maintenance, including by subcontractors on the site; emergency response in case of spills or soil contamination; and worker awareness and training. | Contractors PIU/PMU |
| Ecological impacts | Damage to or removal of established woody vegetation to make way for physical activities (site access) or installations (structures) | Detailed vegetation surveys prior to final design decisions which should avoid or minimize damage to existing vegetation Removal and replanting of mature vegetation, where feasible | PMU / Contractors |
| Construction traffic | Dust, delays to public road users, safety hazards from excessive speed and bad driving, road deterioration | (i) cover construction material while transporting in open trucks; (ii) limit truck speed; (iii) spray water at locations creating dust nuisance to public and workers; (iv) training with code of conduct to all drivers and assistant; (v) limit working hours/days in consultation with nearby sensitive receptors; (vi) ensure full compliance to bidding document and contract provisions; (vii) organize community awareness on safety including training for children; (viii) establish an effective community liaison and grievance reporting and redress mechanism. | Contractors PIU/PMU |
| Public health | Importation of transmissible diseases by construction workers | Covid-19 and related communicable diseases will be handled by the regulations and procedures in force at the time. Prevention of STD transmission is a public health issue, and will be managed as (i) a specific item in the residents’ awareness program, and (ii) a specific item in the contractor’s induction health, safety and environment training for all staff and workers. | Contractors PIU/PMU Local Health Center of the Government |
| Occupational health and safety | A variety of risks associated with both small-scale construction and operating heavy machinery | These risks can be mitigated by standard measures, including (i) keep equipment in good working condition, and properly maintaining it; (ii) ensure all equipment operators are fully qualified and experienced, orient them regularly; (iii) include a full range of health and safety requirements in the bidding and contract documents, including the need for at least one site engineer to have health and safety qualifications; first aid equipment and a minimum number of qualified first aiders amongst site workers; arrange on-site nurse or health worker and establish a medical room with basic health facility to treat trauma and accidents. This is important for an island without a hospital or health center; adopt risk assessment procedures; and emergency protocol in case of accidents; (iv) a requirement for the contractors to develop and implement a health and safety plan; and (v) ensure that the contractors provides health insurance for all staff and workers as well as complying with relevant Maldivian regulations and ADB policy on worker’s health and safety and labor wellbeing. | Contractors PIU/PMU Local Health Center of the Government |
| Compensation for loss of or access to assets | Temporary restrictions on use of or access to public property or private property due to construction works, e.g., closure of streets | For private property, financial compensation using procedures detailed in the project’s RF. For public property, information for users and guidance on alternatives. Active GRM accessible to stakeholders | PMU |
| Operation Phase |  |  |  |
| Surface and groundwater | Impacts will be beneficial, by design | Inspect and maintain drains | PMU / City Council |

Annex B: Environmental Monitoring Plan from ADB Initial Environmental Examination

| Topic | Parameter to be Monitored | Location | Method | Frequency | Responsibility |
| --- | --- | --- | --- | --- | --- |
| Construction Phase |  |  |  |  |  |
| Air quality | Airborne dust | Earthworks sites Along all haul routes on unpaved roads | Particulate measurement to establish pre-works background levels; Visual inspection during active operations; Keep a Volumetric Dust Sampler at site curing work period | Pre-construction baseline under typical range of traffic, wind and rain; Daily; Use meters if controls (watering) ineffective or complaints received | Contractors PIU |
|  | Vehicle and equipment emissions | At fixed and mobile equipment, including trucks | Visual inspection for excessive smoke Get a green sticker on quality of exhaust | Daily for visual inspection Once a year | Contractors PIU |
| Noise | Ambient noise | Other locations if complaints received | Use portable Decibel Meter | Prior to start of excavation work; Daily, if noise is considered a problem by local residents | Contractors PIU |
| Vibration | Condition of fragile properties adjacent to access roads | At any pre-identified locations | Visual inspection | Prior to start of haul traffic; As and when alerted by property owners | Contractors PIU |
| Surface water quality | Turbidity | Drainage outlets from work sites if problem observed visually | Visually; if required, use turbidity tube | During all heavy rain events | Contractors PIU |
| Vegetation / habitat (onshore) | Damage or degradation of established woody vegetation | All areas adjacent to haul routes and work sites | Visual inspection, with time-stamped photos | Prior to start of all works; Daily | Contractors PIU |
| Habitat (tidal zone) | Ecological condition | Representative locations adjacent to all coastal work sites | Repeat survey of ecological conditions | Prior to start of works; Monthly during construction | PMU (through service contract) |
| Fuel & oil storage & handling | Bulk fuel storage facilities and arrangements Refuelling procedures Vehicle maintenance procedures, specifically collection & disposal of engine and hydraulic oils and used oil filters | Contractor’s compound / workshop On-site locations where equipment is refuelled (e.g. excavators) | Visual inspection, with time-stamped photos | Weekly | Contractors PIU |
| Waste management & site housekeeping | All aspects of waste management & site housekeeping: separation, storage, disposal | Contractor’s compound / workshop; Construction sites | Visual inspection, with checklist, time-stamped photos | Weekly | Contractors PIU |
| Labor camp | Facilities Physical condition Sanitation & hygiene | All labor camps | Visual inspection, with checklist, time-stamped photos | Weekly | Contractors PIU |
| Worker safety & health | Use and condition of PPE Safe working practices First aid equipment Fire extinguishers | All active work sites All vehicles including subcontractors | Visual inspection, with checklist, time-stamped photos | Informally, every day Formally, with checklist, every week | Contractors PIU |
|  | Transmissible diseases | Staff and workers, local community | Health records | Monthly | Contractors, in liaison with local health authorities |
| Community safety & health | Disturbance, accidents, health impacts from construction activities | Next to and near all work sites and access routes | Reports from local health authorities Liaison with local government Complaints through GRM | Continuous | Contractors PIU |
| Construction materials | Condition of stockpiles management, compliance with operating plans such as cover, drain, barricading | Stockpiles used to supply construction aggregates | Visual inspection, with checklist, time-stamped photos | Prior to first use of stockpile Weekly during use | Contractors PIU |
| Construction traffic | Driver qualifications Driver training & awareness Vehicle condition Correct loading and sheeting Driving behavior | Site access tracks Public roads | Check of documents; Check of attendance at induction / safety training; Vehicle inspection; Visual observation; Review of grievances | Before start of work for the subproject; Daily | Contractors PIU |
| Public roads | Restricted use, temporary closure | Haul routes, work sites | Record of times and locations | Every time restrictions needed | Contractors PIU |
|  | Condition | Routes used by heavy construction traffic | Visual inspection | Prior to start of haul traffic; Weekly | Contractors PIU |
| Community liaison | Existence of community liaison mechanism and plan Effectiveness of liaison and grievance redress mechanism | All communities affected by construction | Check of documentation; Meetings with designated community coordinator; Review of grievances and their resolution | Prior to start of operations; Weekly; Continuous review of grievances | PMU Contractors PIU |
| Site clean-up | Condition of all locations and facilities used by contractor | All work sites All site access tracks All roads and bridges used by heavy construction traffic Contractors’ camps, compounds and workshops Residual material stockpile and spoil management area | Visual inspection with time-stamped photos | Prior to start of operations (condition survey); After site clean-up | Contractors PMU |
| Operation Phase |  |  |  |  |  |
| Drains (Kulhudhuffushi) | Condition and performance | Outfalls and inspection pits All open drainage facilities, e.g. bioswale | Visual inspection with time-stamped photos | After all major rainfall events | PMU / local government |
| Groundwater (Kulhudhuffushi) | Depth to watertable Water quality (salinity) at different depths | Representative wells and boreholes | Electrical conductivity (EC) of samples from different depths | Monthly | PMU / local government |

Annex C: EMP from Environmental Assessment from the Government of Maldives

The Environmental Impact Assessment (EIA) screening for the project has already been completed by the Environmental Regulatory Authority (ERA). Based on the outcome of the screening, an Environmental Management Plan (EMP) will be prepared to address the identified environmental management requirements.

Annex D: ERA EMP Approval Conditions

Once the EMP is reviewed and approved by the ERA, all resulting conditions and requirements must be incorporated into the Site Environmental Management Plan (SEMP). The SEMP shall be developed by the Contractor and submitted for approval before the commencement of site mobilization.

Annex E: Template for Site-Specific Environmental Management Plan from ADB IEE

| Topic/ Potential Impact | Mitigation, Management and Enhancement Measures | Means of Verification | Responsibility | Monitoring Procedure | Relevant Location (Chainage) |
| --- | --- | --- | --- | --- | --- |
| - Environmental, Social, Health and Safety Management |  |  |  |  |  |
| 1. Responsibilities and liabilities | Adjust this SSEMP to the specific project, define the frequency of the monitoring procedure and share it with PMU and ADB. Identify if further Management Plans have to be prepared. | Final project specific SSEMP | Contractor | Monitor and record the management of the Environmental, Social, Health and Safety (ESHS) topics periodically |  |
|  | Ensure that all workers, suppliers and subcontractors are familiar with and comply with the requirements and specifications of this SSEMP. | Induction performed and recorded | Contractor | Report the induction event (participants, information shared etc.) |  |
| 2. ESHS Management | Define all organizational and technical provisions to satisfy and follow up the specifications of the SSEMP (e.g. resources, documentation) | Requirements for the ESHS management are defined | Contractor | Once, prior to finalization of project specific SSEMP |  |
|  | Make sure that the Site Manager/Supervisor has experience in dealing with ESHS management. Give authority for stopping of works if non-conformities are identified. Appoint qualified EHS officer. Communicate with the relevant authorities the ESHS staff responsible. | The Site Manager has experience in dealing with ESHS issues of similar projects; Qualified EHS officer on site | ContractorPIU/PMU | Once, prior to selection of Site Manager. Weekly inspection reports. |  |
| 3. Code of Conduct | Establish workers Code of Conduct taking into consideration safety rules, substance abuse, environmental sensitivity, communicable diseases, gender issues (sexual harassment), respect for local beliefs and customs, community interactions etc. | Workers Code of Conduct is in place and rules shared with personnel | Contractor PIU/PMU | Punishable or misconduct behaviors are reported and communicated Check grievance records |  |
| 4. ESHS Training | Provide Health and Safety (H&S) Induction and Training to the workforce regarding H&S risks and mitigation measures (including indirect workers) tailored to project scope. | Training performed and recorded | ContractorPIU | Check training records |  |
|  | Awareness raising regarding community health and safety to the local communities through campaigns (e.g. schools) | Awareness raising campaigns performed and recorded | ContractorPIU | Check information material produced |  |
| - Protection of the Environment and People |  |  |  |  |  |
| 5. Protection of adjacent areas | Restrict excavation activities during periods of intense rainfall. Use silt traps to reduce the risk of sediment moving off site. | No excavation during intense rainfall and when site is slippery | ContractorPIU | Site inspection | Add location of silt trap |
|  | Create cutoff ditches to prevent water from entering excavations, if needed. | No surface water entering excavations | Contractor | Random site inspection |  |
|  | Ensure that means of protection are in place to avoid or minimize adverse effects on vegetation, soils, groundwater and surface water, biodiversity, natural drainage and the water quality in areas within the works area. Construction methods to minimize impacts to the extent possible. | No impacts identified in the adjacent environment | ContractorPIU | Regular (daily data reported through monthly report) Monitoring of adjacent natural resources. | Add location for each particular type of impact. |
|  | Ensure that work site boundaries and limits are in accordance with plans agreed in advance. All construction activities should be carried out within boundaries. | Site boundaries and limits on site | Contractor | Site inspections | Add coordinate of work area |
|  | Ensure no works in wetland areas. | No wetland exists in the work area | Contractor | Keep vigilant on waterlogging due to construction work | Add potential waterlogging location within the work area |
| 6. Selection of stockpile sites and access road | Select specific, limited areas for stockpiling and construction of access tracks, and obtain full authorization before construction. | Designated areas selected | ContractorPIU | Once during site selection and monthly during monitoring | Add potential stockpile location within the work area |
| 7. Pollution prevention | Ensure all works carried out minimize pollution risk (e.g. liquid effluents; air emissions; noise and vibration management; vehicle and equipment maintenance and selection; fuel, oil and chemical storage and handling.) including the whole duration of the project. | Potential for pollution is minimal | ContractorPIU | Weekly inspection reports | Add location of sensitive receptors and monitoring station. |
| 8. Effluents | Ensure appropriate containment and storage of construction wastewater, including sanitary water. No untreated effluent is discharged. | Wastewater discharge only after keeping in settling pond, and regular sludge management | Contractor/PIU | Regular site inspection | Location of settling pond |
| 9. Atmospheric emissions and dust | Use only vehicles in appropriate technical condition. Provide emissions control equipment where applicable (e.g. filters). | Technical Specification Sheet | ContractorPIU | Prior to commencement of works and each time new equipment/vehicle is used at the site. |  |
|  | Ensure vehicles are switched off when not in use. Sensitize drivers. | Engines switched off | Contractor | Site inspection |  |
|  | Best practice to ensure minimization of dust emissions (e.g. proper stockpiling, spraying water etc.) during dry and windy conditions and cover during transportation. | Watering conducted, no dust emissions are observed, no workers’ or residents’ grievances | Contractor PIU | Regular site inspection |  |
|  | Ensure speed limits on site. Sensitize drivers. | Speed signs installed; residents’ grievances | Contractor | Random site inspection |  |
| 10. Noise and vibration | Avoid operations and vehicle movements at night. Sensitize drivers. | No work conducted between 10pm and 7 am/ no grievances received | ContractorPIU | Random site inspection, review of filed grievances, interaction with community |  |
|  | Set traffic speed limits. Sensitize drivers. | Speed limit signs Driver Training Records as part of Induction training | ContractorPIU | Random site inspection, Review of training records |  |
|  | Locate stationary equipment (such as power generators) as far as possible from nearby receptors (e.g. worker resting areas, populated areas and environmentally sensitive areas). | Distances between equipment and receptors are kept Cover the generators to suppress noise | Contractor | Once prior to commencement of works Monitor noise levels in case equipment is used |  |
| 11. Waste | Identify waste management facilities and waste management contractors. Ensure disposal through waste contractors licensed for treatment/removal/recycling of each of the waste types. | Waste management through licensed contractors, if feasible Waste Management Plan | Contractor | Inspect waste management facilities Proof of contractors’ certifications |  |
|  | Ensure that all wastes produced are properly collected, segregated, stored, transported and re-used, recycled or disposed of. | Waste collection areas allocated, waste inventories | Contractor | Random site inspection, Review of waste inventories |  |
|  | Minimize waste production to the extent possible. | Records of waste production are kept | Contractor | Monitor (e.g. monthly) the amount of waste produced |  |
|  | Document all waste related operations (type of wastes, quantities produced etc.). | Storage, transport and treatment of waste is documented | Contractor | Document inspection |  |
|  | Appropriate and safe storage of fuels, construction materials, wastes and any other potentially polluting materials. | Safe storage of materials, Spill remediation equipment in place | Contractor | Random site inspection Weekly site inspection reports |  |
| 12. Vegetation clearing | Limit vegetation clearing to areas within the site boundary where it is strictly necessary. | Vegetation clearing minimal | Contractor | Random site inspection |  |
|  | Describe the methods of vegetation clearance. | Do not use fires or chemicals for vegetation clearance | Contractor | Site inspection during site clearance |  |
|  | Avoid clearing mature trees and any protected species. | No mature trees at site to clear | Contractor | Visual inspection |  |
|  | Avoid off-road vehicle traffic. Use existing roads. Sensitize drivers | No off-road traffic | Contractor | Random site inspection |  |
| 13. Biodiversity | Avoid disturbance of natural habitats. | Disturbance of habitats avoided No important habitat in the work area | Contractor | Inspection of construction practices. |  |
| 14. Erosion and sediment transport | Ensure preventive erosion control measures are applied (e.g. plan to retain grass and other vegetation, use of natural contours for roads and drainage networks, create drainage channels). | Preventive erosion control measures in place | ContractorPIU | Random site inspection to check if measures where applied |  |
|  | Ensure appropriate storage of topsoil. After construction, use topsoil as backfill for restoration of the area according to detailed Site Restoration Plan. | Site Restoration Plan Topsoil stored and re-used | ContractorPIU | Monitor if topsoil is properly stored |  |
|  | Optimal stockpiling. | Stockpile height limited and free from erosion and contamination | Contractor PIU | Random site inspection |  |
| 15. Site rehabilitation | Ensure revegetation and restoration of cleared areas after construction. | Revegetation completed | Contractor PIU | One-time inspection after construction |  |
|  | Ensure that rehabilitated areas do not pose health and safety risks (e.g. holes, ponds). | Reinstatement completed | Contractor PIU | One-time inspection after construction |  |
|  | Reinstate construction working area after construction activities are completed. | Reinstatement completed | Contractor PIU | One-time inspection after construction |  |
|  | Rehabilitate storage sites and access roads, where applicable. | Rehabilitation completed | Contractor | One-time inspection after construction |  |
| - Health and Safety |  |  |  |  |  |
| 16. Health and Safety Plan | Develop a Health and Safety Plan. | HS Plan in place | Contractor PIU | Monitoring of Contractor’s measures |  |
| 17. Accident reporting procedure | Ensure all H&S related incidents (e.g. observations, accidents) on site are recorded and followed up effectively. | Incident recording process in place | Contractor PIU | Check incident/accident records |  |
| 18. Personal protective equipment | Ensure the provision of Personal Protective Equipment (PPE) for workers (hardhats, masks, safety glasses, safety boots etc. as appropriate). | PPE used by everyone on site | Contractor PIU | Random site inspection |  |
| 19. Emergency scenarios prevention | Ensure immediate cleaning of any spills and remediation of contaminated areas after construction. | Workers trained | ContractorPIU | Random site inspection after spill events One-time inspection after construction |  |
|  | Provide necessary prevention equipment on site in line with applicable regulations to respond to emergency scenarios, e.g. fire, floods, natural hazards etc. | Prevention equipment in place | Contractor | Regular site inspection |  |
|  | Maintain high standard in housekeeping on site. Construction materials and light equipment should be stored properly. | Visual verification of good housekeeping on-site | Contractor PIU | Random site inspection |  |
| 20. First-aid | Ensure minimum first aid provisions on site. (suitably stocked first-aid kits; at least one person trained in first aid at each work site, respectively an adequate number of first-aid helpers; ensure that staff and workers are informed about first-aid arrangements) | Suitable first aid kits on site Ensure the presence of first aid helpers in all shifts | Contractor PIU | Regular monitoring of first aid kits |  |
| 21. Access to health care and training | Ensure the workforce has access to primary healthcare on site, providing prescriptions and vaccinations. | Medical room with health worker for healthcare available on site | Contractor PIU | Random site inspection |  |
|  | In all cases, determine the location and access routes to the nearest functional hospital, medical clinic or health center and establish an evacuation plan for casualties. | Medical centers in the proximity of the site. | ContractorPIU | Medical centers in the proximity of the site identified once prior to commencement of works |  |
| 22. Hygiene, accommodation and food | Ensure provision of H&S and hygienic and sanitary facilities at the site, including shaded welfare areas, showers, changing rooms and potable water. Ensure toilets and changing rooms are separated between male and female employees. | Appropriate H&S and sanitary facilities provided at site | Contractor | Random site inspection |  |
|  | Ensure the provision of adequate space, supply of water, adequate sewage and garbage disposal system, appropriate protection against heat, cold, damp, fire and disease-carrying animals, adequate sanitary and washing facilities, adequate lighting, and basic medical services, in accordance with all applicable health and safety regulations and norms. | Appropriate conditions for workers on site following labor camp standards attached to CA | Contractor PIU | Worker’s camp established Record kept via grievance mechanism |  |
|  | Report any occurrence of any communicable diseases amongst the workforce (Covid-19, STDs, Tuberculosis and Hepatitis B and C). Sensitize workers. | Communicable Diseases Register | Contractor | Review of diseases register and disease prevention program if available. |  |
| - Local labour and relations with local communities |  |  |  |  |  |
| 23. Labor conditions | Ensure legal labor standards as per the International Labor Organization regulations, and ADB and government policies (child/forced labor, sexual assault, no discrimination, equal opportunities, working hours, minimum wages) are met. | Grievance Mechanism Records, Training recorded | Contractor | Inspection reports (also from labor authorities), Review of grievance register and training record |  |
|  | Ensure that all direct and indirect workers have access to and are aware about the Grievance Mechanism where they can raise workplace relevant complaints anonymously. | Grievance Mechanism in place and grievances recorded | Contractor PIU | Review of grievance register |  |
|  | Ensure all workers have the same rights and are treated equally. | Non-discrimination policy in place | Contractor PIU | Random site inspection Grievance mechanism log |  |
| 24. Local recruitment | Ensure local communities are preferred for the supply of goods and services to the subproject and subproject personnel, where appropriate. | Local Procurement and Employment Records | Contractor | Review procurement and employment rules and records |  |
| 25. Transport | Organize means of transportation for worker if their camp is in distance. | Carpools/ buses used | Contractor | None |  |
| 26. Community interaction | Engage / communicate / inform affected communities. Ensure good communication and consultation with local authorities and communities regarding all activities. | Minutes of Meetings Grievance Mechanism | Contractor / PIU | Review of grievance register Minutes of consultation meetings |  |
|  | Initiate an efficient Grievance Mechanism to allow potentially affected individuals to raise their concerns. | Grievance Mechanism in place, grievances recorded | Contractor / PIU | Review of grievance register |  |
|  | Engage with the local community and potential affected households to understand their needs and identify the risk of damage to their livelihoods by subproject activities (e.g. exclusion from pasture land, lack of access to water, slope failure risk during excavation). Should impacts be unavoidable, a timely and fair compensation should be given to all affected persons in accordance with project’s Resettlement Framework (RF). | Minutes of Meetings Grievance Mechanism records. Management Plan for Land Acquisition and Compensation if needed | Contractor/ PIU | Review of grievance register and meeting minutes |  |
| 27. Damage to people and property | Ensure all contractors implement codes of conduct concerning employment and workforce behavior (including but not limited to safety rules, zero tolerance for substance abuse, environmental sensitivity of the area, dangers of sexually transmissible diseases and HIV/AIDS, gender equality and sexual harassment, respect for the beliefs and customs of the populations and community relations in general). | Workers Code of Conduct Grievance Mechanism records | Contractor PIU | Worker interviews, Review of grievance log Record of identified cases |  |
|  | Ensure that site areas are provided with appropriate security, fencing, signage and lighting. Use hazard notices / signs / barriers to protect children and other vulnerable people from harm and prevent access to non-workers. | H&S planning of construction site approved, items installed | ContractorPIU | Random and routine site inspection |  |
| 28. Land acquisition and land take | Engage with the local community to understand local land ownership and land use. Avoid to the extent possible land take of both formal and informal land owners/land users. If land take is inevitable, no forced eviction should take place. Should impacts be unavoidable, a timely and fair compensation should be given to all affected persons in accordance with project’s Resettlement Framework (RF). Owners should be compensated prior to access to land. | Grievance Mechanism Management Plan for Land Acquisition and Compensation if needed | PIU / Contractor | Once during site selection Review of grievance log Follow up of land acquisition/compensation process |  |
| 29. Traffic management | Ensure safe driving by subproject personnel (e.g. through training/induction). | Driver Training Records as part of Induction training | Contractor | Review of training records |  |
|  | Target signage and outreach activities to improve public awareness of traffic changes and potential hazards for high-risk sections of public roads, including near the site and contractor’s compounds. | Warning and safety signs, traffic signs Minutes of Meetings | Contractor | Inspection of traffic diversion, Review of grievance register |  |
| 30. Fossils/ Archaeological Chance Finds | Establish specific procedures to manage the protection of archaeological and historical sites, chance finds and fossils. Ensure all finds of physical cultural heritage (e.g. graves, old ceramic, old building fragments) are reported immediately to the relevant authority and avoid excavation in the ultimate neighborhood of a chance find, fence the chance find and await instructions from the competent authority. | Training records, records about chance finds | Contractor PIU PMU | Site inspection |  |

### 6.  Certificates

6.1  Form of Completion Certificate

Contract: [. . . . .insert name of contract and contract identification details.  . . . . ]

Date:

Certificate No.:

To:  [. . . . .insert name and address of contractor.  . . . . ]

Dear Ladies and/or Gentlemen,

Pursuant to GCC Clause 24 (Completion of the Facilities) of the General Conditions of the Contract entered into between yourselves and the Employer dated [. . . . .insert date. . . . . ], relating to the [. . . .brief description of the Facilities . . . .], we hereby notify you that the following part(s) of the Facilities was (were) complete on the date specified below, and that, in accordance with the terms of the Contract, the Employer hereby takes over the said part(s) of the Facilities, together with the responsibility for care and custody and the risk of loss thereof on the date mentioned below.

1.	Description of the Facilities or part thereof:  [. . . .description . . . .]

2.	Date of Completion:  [. . . .date . . . .]

However, you are required to complete the outstanding items listed in the attachment hereto as soon as practicable.

This letter does not relieve you of your obligation to complete the execution of the Facilities in accordance with the Contract nor of your obligations during the Defect Liability Period.

Very truly yours,

[. . . .Signature . . . .]

Project Manager

6.2  Form of Operational Acceptance Certificate

Contract: [. . . . .insert name of contract and contract identification details.  . . . . ]

Date:

Certificate No.:

To:  [. . . . .insert name and address of contractor.  . . . . ]

Pursuant to GCC Subclause 25.3 (Operational Acceptance) of the General Conditions of the Contract entered into between yourselves and the Employer dated [. . .date. . .], relating to the [. . .brief description of the facilities. . .], we hereby notify you that the Functional Guarantees of the following part(s) of the Facilities were satisfactorily attained on the date specified below.

1.	Description of the Facilities or part thereof:  [. . . description . . .]

2.	Date of Operational Acceptance:  [. . . date . . .]

This letter does not relieve you of your obligation to complete the execution of the Facilities in accordance with the Contract nor of your obligations during the Defect Liability Period.

Very truly yours,

[. . . .Signature . . . .]

Project Manager

### 7.  Change Orders

7.1	Change Order Procedure

7.1.1	General

7.1.2	Change Order Log

7.1.3	References for Changes

7.2.	Change Order Forms

7.2.1	Request for Change Proposal

7.2.2	Estimate for Change Proposal

7.2.3	Acceptance of Estimate

7.2.4	Change Proposal

7.2.5	Change Order

7.2.6	Pending Agreement Change Order

7.2.7	Application for Change Proposal

### 7.1. 	Change Order Procedure

### 7.1.1  General

This section provides samples of procedures and forms for implementing changes in the Facilities during the performance of the Contract in accordance with GCC Clause 39 (Change in the Facilities) of the General Conditions.

### 7.1.2 	Change Order Log

The Contractor shall keep an up-to-date Change Order Log to show the current status of Requests for Change and Changes authorized or pending. Entries of the Changes in the Change Order Log shall be made to ensure that the log is up-to-date. The Contractor shall attach a copy of the current Change Order Log in the monthly progress report to be submitted to the Employer.

### 7.1.3	References for Changes

(1)	Request for Change as referred to in GCC Clause 39 shall be serially numbered CR-X-nnn.

(2)	Estimate for Change Proposal as referred to in GCC Clause 39 shall be serially numbered CN-X-nnn.

(3)	Acceptance of Estimate as referred to in GCC Clause 39 shall be serially numbered CA-X-nnn.

(4)	Change Proposal as referred to in GCC Clause 39 shall be serially numbered CP-X-nnn.

(5)	Change Order as referred to in GCC Clause 39 shall be serially numbered CO-X-nnn.

Note:

(a)	Requests for Change issued from the Employer’s Home Office and the Site representatives of the Employer shall have the following respective references:

Home Office	CR-H-nnn

Site		CR-S-nnn

(b)	The above number “nnn” is the same for Request for Change, Estimate for Change Proposal, Acceptance of Estimate, Change Proposal and Change Order.

### 7.2	Change Order Forms

### 7.2.1  Request for Change Proposal Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

With reference to the captioned Contract, you are requested to prepare and submit a Change Proposal for the Change noted below in accordance with the following instructions within [  number  ] days of the date of this letter [or on or before (  date  )].

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Number  ]

3.	Originator of Change:

Employer:  [Name]

Contractor (by Application for Change Proposal No. [Number Refer to Annex 6.2.7])

4.	Brief Description of Change:  [  Description  ]

5.	Facilities and/or Item No. of equipment related to the requested Change:  [  Description  ]

6.	Reference drawings and/or technical documents for the request of Change:

Drawing No./Document No.		Description

7.	Detailed conditions or special requirements on the requested Change:  [  Description  ]

8.	General Terms and Conditions:

(a)	Please submit your estimate showing what effect the requested Change will have on the Contract Price.

(b)	Your estimate shall include your claim for the additional time, if any, for completing the requested Change.

(c)	If you have any opinion that is critical to the adoption of the requested Change in connection with the conformability to the other provisions of the Contract or the safety of the Plant or Facilities, please inform us in your proposal of revised provisions.

(d)	Any increase or decrease in the work of the Contractor relating to the services of its personnel shall be calculated.

(e)	You shall not proceed with the execution of the work for the requested Change until we have accepted and confirmed the amount and nature in writing.

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

7.2.2   Estimate for Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

With reference to your Request for Change Proposal, we are pleased to notify you of the approximate cost to prepare the below-referenced Change Proposal in accordance with GCC Subclause 39.2.1 of the General Conditions.  We acknowledge that your agreement to the cost of preparing the Change Proposal, in accordance with GCC Subclause 39.2.2, is required before estimating the cost for change work.

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Number  ]

3.	Brief Description of Change:  [  Description  ]

4.	Scheduled Impact of Change:  [  Description  ]

5.	Cost for Preparation of Change Proposal:  [  insert costs, which shall be in the currencies of the contract  ]

(a)	Engineering	(Amount)

(i)	Engineer		 hours (hrs) x 	 rate/hr =

(ii)	Draftsperson		 hrs x 	 rate/hr =

Sub-total		 hrs

Total Engineering Cost

(b)	Other Cost

Total Cost (a) + (b)

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

7.2.3  Acceptance of Estimate Form

[ Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [ Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We hereby accept your Estimate for Change Proposal and agree that you should proceed with the preparation of the Change Proposal.

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Request number/revision  ]

3.	Estimate for Change Proposal No./Rev.:  [  Proposal number/revision  ]

4.	Acceptance of Estimate No./Rev.:  [  Estimate number/revision  ]

5.	Brief Description of Change:  [  Description  ]

6.	Other Terms and Conditions:  In the event that we decide not to order the Change accepted, you shall be entitled to compensation for the cost of preparing the Change Proposal described in your Estimate for Change Proposal mentioned in para. 3 above in accordance with GCC Clause 39 of the General Conditions.

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

7.2.4  Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

In response to your Request for Change Proposal No. [Number], we hereby submit our proposal as follows:

1.	Title of Change:  [  Name  ]

2.	Change Proposal No./Rev.:  [  Proposal number / revision ]

3.	Originator of Change:	Employer:  [ Name  ] / Contractor:  [  Name  ]

4.	Brief Description of Change:  [  Description  ]

5.	Reasons for Change:  [  Reason  ]

6.	Facilities and/or Item No. of Equipment related to the requested Change:  [  Facilities  ]

7.	Reference drawings and/or technical documents for the requested Change:

[  Drawing/Document No./Description  ]

8.	Estimate of increase/decrease to the Contract Price resulting from the Change Proposal:

Amount

[ insert  amounts in the currencies of the Contract ]

(a)	Direct material

(b)	Major construction equipment

(c)	Direct field labor (Total 	 hrs)

(d)	Subcontracts

(e)	Indirect material and labor

(f)	Site supervision

(g)	Head office technical staff salaries

Process engineer		 hrs @ 	 rate/hr

Project engineer		 hrs @ 	 rate/hr

Equipment engineer		 hrs @ 	 rate/hr

Procurement		 hrs @ 	 rate/hr

Draftsperson		 hrs @ 	  rate/hr

Total			hrs

(h)	Extraordinary costs (computer, travel, etc.)

(i)	Fee for general administration, 	 % of Items

(j)	Taxes and customs duties

Total lump sum cost of Change Proposal		[  Sum of items (a) to (j)  ]

Cost to prepare Estimate for Change Proposal	 	[  Amount payable if Change is not accepted  ]

9.	Additional time for Completion required due to Change Proposal

10.	Effect on the Functional Guarantees

11.	Effect on the other terms and conditions of the Contract

12.	Validity of this Proposal:  within [Number] days after receipt of this Proposal by the Employer

13.	Other terms and conditions of this Change Proposal:

(a)	You are requested to notify us of your acceptance, coMMTnts or rejection of this detailed Change Proposal within [Number] days from your receipt of this Proposal.

(b)	The amount of any increase and/or decrease shall be taken into account in the adjustment of the Contract Price.

(c)	Contractor’s cost for preparation of this Change Proposal: [ . . . .insert amount. This cost shall be reimbursed by the employer in case of employer’s withdrawal or rejection of this Change Proposal without default of the contractor in accordance with GCC Clause 39 of the General Conditions . . . . ]

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

7.2.5  Change Order Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We approve the Change Order for the work specified in the Change Proposal (No. [  number  ]), and agree to adjust the Contract Price, Time for Completion, and/or other conditions of the Contract in accordance with GCC Clause 39 of the General Conditions.

1.	Title of Change:  [  Name  ]

2.	Change Request No./Rev.:  [  Request number / revision  ]

3.	Change Order No./Rev.:  [  Order number / revision  ]

4.	Originator of Change:	Employer:  [Name] / Contractor:  [  Name  ]

5.	Authorized Price:

Ref. No.:  [  Number  ]	Date:  [  Date  ]

Foreign currency portion [  Amount  ]  plus Local currency portion [  Amount  ]

6.	Adjustment of Time for Completion

None		Increase [  Number  ] days	 	Decrease [  Number  ] days

7.	Other effects, if any

Authorized by:  		Date:

Employer

Accepted by:  		Date:

Contractor

7.2.6  Pending Agreement Change Order Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We instruct you to carry out the work in the Change Order detailed below in accordance with GCC Clause 39 of the General Conditions.

1.	Title of Change:  [  Name  ]

2.	Employer’s Request for Change Proposal No./Rev.:  [  number/revision  ]	dated:  [ date  ]

3.	Contractor’s Change Proposal No./Rev.:  [  number / revision  ]	dated:  [ date ]

4.	Brief Description of Change:  [ Description ]

5.	Facilities and/or Item No. of equipment related to the requested Change:  [ Facilities ]

6.	Reference Drawings and/or technical documents for the requested Change:

[  Drawing / Document No. / Description  ]

7.	Adjustment of Time for Completion:

8.	Other change in the Contract terms:

9.	Other terms and conditions:

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

7.2.7  Application for Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We hereby propose that the work mentioned below be treated as a Change in the Facilities.

1.	Title of Change:  [  Name  ]

2.	Application for Change Proposal No./Rev.:  [  Number / revision  ]	dated:  [  Date  ]

3.	Brief Description of Change:  [  Description  ]

4.	Reasons for Change:

5.	Order of Magnitude Estimation (amount in the currencies of the Contract): [  Amount  ]

6.	Scheduled Impact of Change:

7.	Effect on Functional Guarantees, if any:

8.	Appendix:

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

### 8.  Personnel Requirements

Using Form PER - 1 and PER - 2 in Section 4 (Bidding Forms), the Bidder must demonstrate that it has personnel who meet the following requirements:

| No. | Position | Total Work Experience [years] | Experience In Similar Work [years] |
| --- | --- | --- | --- |
| 1 | Project Manager/Team Leader - Minimum Bachelor's Degree in Project Management/Construction Management/Civil/Environmental Engineering/Geography/Hydrology or related field - Holding Master’s degree will be an advantage - Experience in project management in undertaking similar projects - Previous relevant experience working in the Maldives will be an added advantage. - Knowledge of issues around environmental sustainability and climate change adaptation in Maldives will be an advantage. | 7 | 5 |
| 2 | Design Engineer - Minimum Bachelor’s degree in Civil/Structural Engineering - Proven experience in undertaking detailed design is required. - Previous relevant experience working in the Maldives. - The contractor must submit a commitment letter, signed by the designated design engineer, confirming their availability to actively participate in the project throughout its entire duration. | 7 | 5 |
| 3 | Design Architect - Minimum Bachelor's degree in Architecture - Proven experience in undertaking detailed design is required. - Previous relevant experience working in the Maldives. - The contractor must submit a commitment letter, signed by the designated design architect, confirming their availability to actively participate in the project throughout its entire duration. | 7 | 5 |
| 4 | Field/Site Engineer - Minimum Diploma in Civil Engineering - Minimum 3 years of experience in site management or related works. | 3 | 3 |
| 5 | Quantity Surveyor - Minimum Diploma in Quantity Survyeing with experience in formulating BOQs for similar civil infrastructure related projects. | 3 | 3 |
| 6 | Surveyor - Minimum Diploma in Surveying/Civil Engineering - Minimum 3 years' experience in conducting land surveys | 3 | 3 |

Using Form EXP-6 in Section 4 (Bidding Forms), the Bidder must demonstrate that it has EHS personnel who meet the following requirements:

Key Personnel as determined by the EMP and other safeguard management plans

| Item No. | Position/specialization | Relevant academic qualifications | Minimum years of relevant work experience | Minimum time on-site (%FTE) |
| --- | --- | --- | --- | --- |
| 1 | Environment, Health & Safety (EHS) Specialist* | Minimum BSc in environmental management and/or environmental science MSc in environmental management and/or environmental science Certification in construction site EHS management | 5 years | 50% |
| 2 |  |  |  |  |
| 3 |  |  |  |  |

* This position may be split across two persons each focusing on environmental safeguards and OHS.

### 9.  Equipment Requirements

Using Form EQU in Section 4 (Bidding Forms), the Bidder must demonstrate that it has the key equipment listed below:

| No. | Equipment Type and Characteristics | Minimum Number Required |
| --- | --- | --- |
| 1 | Concrete Mixer/ Machine | 1 |
| 2 | Vibrator | 1 |
| 3 | Truck/ Dump Truck | 2 |
| 4 | Excavator/ Barge | 1 |

This value corresponds to .036 mm/hr if the standard Marshall-Palmer Z-R relationship ifs applicable.

https://gpm.nasa.gov/missions/GPM

The nearest substation is 170 m away (Figure 3)

Proposals for a solid state pulse compression system will be taken into consideration if the overall radar performances do satisfy the present operational requirements.

The closest observation range shall be in any case as indicated in specification DWR-38.

Approval by the Employer of the Radar system detailed design study, including the detailed building design, will be necessary prior starting manufacturing or building works.

The site has been surveyed and physical demarcations are placed at the site

Labor camps are not anticipated since worker numbers will be small and are likely to be sourced from and/or accommodated in existing facilities in the local community.