## Main Summary
Summary sheets of B. Fehendhoo Health Center Upgrading Project
# | Description | Sub total | GST | Grand Total
1 | EXTENSION BUILDING
2 | BOUNDARY WALL

## SUMMARY
SUMMARY OF BILLS OF QUANTITIES
CONSTRUCTION OF EXTENSION BUILDING AT B. FEHENDHOO HEALTH CENTER.
Bill No | Description |  | Amount
1 | PRELIMINARIES | Bill no. 01
2 | GROUND WORKS | Bill no. 02
3 | CONCRETE | Bill no. 03
4 | MASONRY AND PLASTERING | Bill no. 04
5 | ROOFING | Bill no. 05
6 | DOORS AND WINDOWS | Bill no. 06
7 | TILING | Bill no. 07
8 | CEILINGS | Bill no. 08
9 | PAINTING | Bill no. 09
10 | ELECTRICAL INSTALLATIONS | Bill no. 10
11 | HYDRAULICS & DRAINAGE | Bill no. 11
12 | AIR CONDITIONING SYSTEM | Bill no. 12
13 | TENDERER'S ADJUSTMENTS | Bill no. 13
Sub total
GST 8%
GRAND TOTAL carried to form of bid

## Extension
BILL OF QUANTITIES
CONSTRUCTION OF EXTENSION BUILDING AT B. FEHENDHOO HEALTH CENTER.
B. FEHENDHOO ISLAND
Updated on 20 July 2025
Item | Description | Unit | Quantity | Rate/ Unit | Rate/ Unit | Total Unit Rate | Amount
|  |  |  | Material | Labour | Rates per Units
BILL No: 01
PRELIMINARIES
1.1 | General Notes
(1) | Abbreviations
m - meter
No - numbers
m³ - cubic meter
m² - square meter
Lm - Linear meter
KG - Kilograms
incl - including
mm - millimeter
dia - diameter
SS - Stainless Steel
GI - Galvanized Iron
1.2 | SIGN BOARD
1 | Size of Sign board must be minimum 2.4X1.2 Meter. | Item | 1
1.3 | CLEAN-UP
1 | Allow for clean-up of completed works and site upon completion. | Item | 1
1.4 | INSURANCE, BONDS,
1 | Insurance as stated in the General Consditions. | Item | 1
1.5 | AS-BUILD DRAWINGS
1 | Preparation and submission of "as-built" Drawings. | Item | 1
1.6 | Site visits
1 | Arrange Site visits to PMU team. Contractor has to arrange following for trips; (a) Speed boat transfer from Male cit B. Fehendhoo/Male city/B. Fehendhoo. Type of Speed boat must be Gulfcraft 36 Touring or Equivalent. (c) Accommodations (2 Air-condition room) for 2 nights per trip at the guest house. | Item | 5
BILL No: 01 PRELIMINARIES
TOTAL OF BILL No: 01 - Carried over to summary
BILL No: 02
GROUND WORKS
2.1 | General
(a) Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, consolidating and disposing surplus soil.
2.2 | Site Clearing
1 | Includes clearing of all trees and bushes complete with stems, roots, Flooring, and the reimbursement fees if applicable. The contractor is to advised to survey the construction site and ensure that all necessary works for site clearing are included and on completion of works. Rates must include diverting all the pipes laid underground within the new building area (Sewer, wastewater, freshwater line and inspection chambers). Also, reallocate all AC outdoor units installed with the new building area, Diverting for All the electrical cable laid on the proposed land. Rates must include to demolition of Ground water well and fill the well, Rain water shed with foundation and clean the Debris, | m² | 250.73
The contractor Must survey the proposed building site before submitting the bid.
2.3 | Excavation
Excavation shall be carried out in all type of materials and by whatever means are necessary accurately to the lines and levels shown in the approved drawing. No blasting of any kind will be permitted. Excavation for foundations and will include timbering of soil faces and dewatering. Excavation quantities are measured to the faces of concrete members. Rates shall include for dewatering, leveling, grading, trimming compacting to faces of excavation, keeping sides plumb, backfilling, consolidating and disposing surplus soil and include for all additional excavation required to place the formwork / shuttering and dewatering the trench for the required days.
1 | Excavation for Footings (F1) | m³ | 6.75
2 | Excavation for Tie beam beams (TB) | m³ | 29.49
2.4 | Back Filling up to ground level.
1 | Rates shall include for: leveling, grading, trimming and compacting as specified. | Item | 1
2.3 | Basement filling Above ground level.
1 | Back filling above ground level in 100mm thick compacted layers of approved back fill soil and disposal of any excess soil and including ramp: rates shall include for leveling, grading, trimming and compaction in 100mm layers of filled areas of excavation | m³ | 45.22
2.4 | Damp Proof Membrane
Cutting and laying in position heavy duty polythene sheets of gauge 500 (not less than 1.5mm thick). Rates shall include for: dressing around and sealing to all penetrations. Apply slurry type waterproofing to all surfaces of concrete below ground level in accordance with manufacturer's instructions.
1 | Damp proof membrane above lean concrete , Footings and Tie beams. | m | 48.33
2 | Damp proof membrane below floor slab | m² | 250.73
3 | Bituminous application to 3 sides of footings, Tie beams & all the side of columns below ground level. | m² | 137.11
2.5 | Connection of Health center Building
1 | Demolition of existing wall to connect new building, ward area, ward toilet and connection of new builing, Rates to be include demolition of walls, plastering of edges, painting and cleaning of debris also include other necessary works required. | m² | 36.15
BILL No: 02 - GROUND WORKS
TOTAL OF BILL No: 02 - Carried over to summary
BILL No: 03
CONCRETE
3.1 | General
Rates shall include for cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wire and other supports, laps and wastage, all reinforcement bars except 6 mm dia bars shall be of deformed high strength bars. 6 mm bar shall be round mild steel bars. Binding wire shall be of 1.6 mm or 1.4 mm soft iron wire. Reinforcement bars shall be cleaned before use i.e. should be free from rust, oil, din, or other coatings that reduces bonds, all reinforced bars and binding wires shall be stored under cover of at least 450 mm above the ground, cutting and bending according to approved manner & the approved working drawing, placing and fixing in position and binding should be as per the approved working drawing, laps in the bars shall be staggered, concrete cover for reinforcement shall not less than 50 mm for substructure, 40 mm for columns & side beams and not more than 30 mm for slab and beam bottoms. Desalinated water shall be used for all purposes, ground water shall not be used.
3.2 | Lean Concrete
Lean concrete shall be 50mm thick & mix ratio shall be 1:2:6 by dry volume. Lean concrete placed at bottom of footing and foundation beam and below plinth for protection according to line and length mentioned in the approved drawing. Quantity measured to the edges of concrete foundation members. Rate shall include of placing any formwork where necessary, batching, mixing, casting in all required items pouring & compacting and curing for 3 days and removal of any formwork include for provision casting of required items & finishing after removal of formwork and additional concrete required to confirm to structural and excavated tolerances and rates shall include supply of all required works
1 | 50 mm thick lean concrete under the footings / strip footing and tie beam with a mix of 1:2:6 | m³ | 2.89
3.3 | Reinforced Concrete
In-situ reinforced concrete to:
*Add water proofing compound / admixture to concrete mix for walls GL and Roof Slabs
3.3.1 | Foundations
1 | Footings, F1 600x600x300mm | m³ | 2.7
2 | Tie Beam, TB 200x250mm | m³ | 7.87
3.3.2 | Ground Floor
1 | RCC Ground Slab 100 mm thick, Ground Slab and Garage ramp area. | m³ | 25.07
2 | Concrete columns C1, 200 x 200mm | m³ | 3.81
4 | Concrete Lintel beams, 150 x 150mm | m³ | 1.17
5 | Concrete Sill beams, 150 x 150mm | m³ | 0.46
3.3.3 | Roof Level
1 | Roof beam, RB, 200x200mm ( Level 1) | m³ | 6.29
2 | Roof beam, RB, 200x200mm ( Level 2) | m³ | 1.3
3 | Concrete columns C2, 200 x 200mm | m³ | 0.73
3.3 | Formwork
(a) Rates shall include for all necessary boarding, supports, erecting, framing, temporary cambering, cutting, perforations for reinforcing bars, bolts, straps, ties, hangers, pipes and removal of formwork. All materials such as plywood, shutter oils and other items and transportation to work place and secure the formwork in highly precise manner guaranteeing straight and smooth concrete edges. Cutting, fixing, bracing and oiling according to line and length as per approved working drawings removal of it after concrete has set without damaging the concrete faces.
3.3.1 | Foundations
1 | Footings, F1 600x600x300mm, (50% of form work) same form work to be use balance 50% Footings | m² | 9
2 | Tie beam, TB 200X250mm | m² | 78.65
3.4.2 | Ground Floor
1 | Concrete columns C1, 200 x 200mm, (50% of form work) same form work to be use balance 50% column | m² | 39
3.4.2 | Roof level
1 | Roof beam, RB, 200x200 ( Level 1 & 2) | m² | 94.38
2 | Concrete columns C2, 200 x 200mm, (50% of form work) same form work to be use balance 50% column | m² | 19.5
3.4.3 | Lintel & Sill Beams
1 | Lintel beams and Sill beams, 150x150mm, (50% of form work) same form work to be use balance | m³ | 7.4
3.5 | Reinforcement
GENERAL : Rates shall include for cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wire and other supports, laps and wastage, all reinforcement bars except 6 mm dia bars shall be of deformed high strength bars. 6 mm bar shall be round mild steel bars. Binding wire shall be of 1.6 mm or 1.4 mm soft iron wire. Reinforcement bars shall be cleaned before use i.e. should be free from rust, oil, din, or other coatings that reduces bonds, all reinforced bars and binding wires shall be stored under cover of at least 450 mm above the ground, cutting and bending according to approved manner & the approved working drawing, placing and fixing in position and binding should be as per the approved working drawing, laps in the bars shall be staggered, concrete cover for reinforcement shall not less than 50 mm for substructure, 40 mm for columns & side beams and not more than 30 mm for slab and beam bottoms.
(b) All reinforcing bars shall be high strength bars.
3.5.1 | Substructure
Footings, F1 600x600x300mm
1 | Steel deformed bars, 12mm dia x 6m | Bars | 32
Tie beam, TB 200x200mm
1 | Steel deformed bars, 12mm dia x 6m | Bars | 114
2 | Steel ring bars, 6mm dia x 6m | Bars | 105
3.5.2 | Ground Floor
Concrete columns C1, 200 x 200mm
1 | Steel deformed bars, 12mm dia x 6m | Bars | 69
2 | Steel ring bars, 6mm dia x 6m | Bars | 64
3.5.3 | Roof level
3.5.3.1 | Attached Beams,
Roof beam, RB, 250x200 mm
1 | Steel deformed bars, 12mm dia x 6m | Bars | 138
2 | Steel ring bars, 6mm dia x 6m | Bars | 127
3.5.3.2 | Concrete columns C2, 200 x 200mm
1 | Steel deformed bars, 12mm dia x 6m | Bars | 14
2 | Steel ring bars, 6mm dia x 6m | Bars | 13
3.5.5 | Floor Slab
1 | 10 mm dia bars @250 C/C, For ground slab | bars | 292
3.5.4 | OTHER CONCRETE WORKS
1 | Fabrication of Concrete sink cupboard at Washing areas, Staff Room, 1.3 Meter length and 600mm width as per drawings, Rates shall include, concrete works tiling of all surfaces, installation of Single ball SS sink with faucet. And Rates shall also include all hydraulic works related to this item. Also rates shall include fixing of timber door panel and shelves. minimum 12mm thick quarts sheets to be installed on the sink cupboard. also tilling as per drawings. | Item | 2
2 | Fabrication of Concrete sink cupboard at Nurse Station, Dirty Utility , 1.3 Meter length and 600mm width as per floorplan, Rates includes, concrete works tiling of all surfaces,installation of 1 ceramic laboratory sink 620x480x255mm, (Cotto or equivalent)with an wall mount elbow operated faucet. And Rates shall also include connecting fresh water, waste water related to this item. Also, rates shallinclude fixing the timber door panel and shelves with PVC role fomica on allsurfaces. Granite sheet to be laid on top of the Sink cupboard. 12mm thick plywood to use for door panels of the cupboard with both side Formica, also tilling as per drawings. | Item | 2
3 | Fabrication of Concrete sink cupboard at private/Critical room and Labour room, 2 Meter length and 600mm width as per floorplan, Rates includes, concrete works tiling of all surfaces,installation of 1 ceramic laboratory sink 620x480x255mm, (Cotto or equivalent)with an wall mount elbow operated faucet. And Rates shall also include connecting fresh water, waste water related to this item. Also, rates shallinclude fixing the timber door panel and shelves with PVC role fomica on allsurfaces. Granite sheet to be laid on top of the Sink cupboard. 12mm thick plywood to use for door panels of the cupboard with both side Formica, also tilling as per drawings. | Item | 2
4 | Completion of a groundwater well with a 120 mm thick top slab, including a 350 mm X 350 mm opening. The well shall have a diameter of 1.2 meters, and the water level must be a minimum of 1.2 meters during low tide, Rates must include the installation of water pump and connect the existing ground water line. | Item | 1
5 | Relocate the rainwater tank as per drawings and connect the rainwater downpipes to the main drainage system. | Item | 1
BILL No: 03 - CONCRETE WORKS
TOTAL OF BILL No: 03 - Carried over to summary
BILL No: 04
MASONRY AND PLASTERING
4.1 | General
Rates shall include for: cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding frames or plates, building in joists, bearers or similar, temporary supports to openings, templates, reinforcement in walls and for all necessary making good. Bedding mortar (mixing ratio 1:4 i.e. cement: manufactured sand) shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance. Masonry work shall be done with approved Machine compact cement blocks (300X150X150) with no defects. Lay in line and length as per approved working drawing Block making (mixing ratio 1:4 i.e. cement: Local sand, Free form salt) shall be of OPC & free form salt.
floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding
Rates shall include for: 25mm groove lines on external surfaces as shown on the drawing. Desalinated water shall be used for all purposes, if ground water is not drinkable.
4.2 | Cement block work
External and external walls
4.2.1 | 127mm (5 inch) wide Hollow blocks, laid on and incl. 1:5 Cement Mortar, tie rods, compression gap filler, nylon / plastic mesh as specified. (mixing ratio 1:4 i.e. cement: river sand, )
1 | Ground Floor (external walls internal walls) of Below Ground Slab. | m² | 78.65
2 | Ground Floor (external and internal walls) of Above Floor Slab. | m² | 436
4.3 | Plastering
GENERAL: Interior and Exterior: Plaster All masonry wall have smooth finishing of 18 mm thick cement plastering with mix ratio 1:4 (i.e. cement: River Sand), plastering material shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance. Plastic net should be provided wherever concrete surface and masonry meets, and cracks are unacceptable. Regular curing up to 7 days must be done, edges of doors, windows and ventilators included.
4.3.1 | 25mm thick cement plastering (2 coat) on external walls and 18mm thick cement plastering on internal walls and concrete surfaces with 1:4 Cement mortar mix as specified incl. wire mesh at joints of concrete surfaces and walls (first, second coats).
1 | Ground floor ( below Floor slab) | m² | 157.3
2 | Ground floor ( Above Floor slab) | m² | 872
3 | Removal of wall tiles of existing ward toilet, plastering of the wall. | m² | 11.8
4.4 | Dry wall partition
100mm thick dry wall partition, 50X75mm Timber frame (600mm c/c Vertical, 1200mm c/c Horizontal) with 9mm thick Shera board. Rates includes to fabricate partition as per manufactures instructions. All the timber must be treated or applied wood preservative oil before fixing the Gypsum board.
1 | Dry wall Partition, up to the ceiling. | m² | 78.67
2 | Dry wall Partition, 2.6M from FFL. | m² | 8.32
3 | Aluminum Partition wall , up to the ceiling. Aluminum frame must be minimum 75X50mm With an 8mm thick laminated Clear glass | m² | 14.41
4 | Boxing of AC pipe lines as per drawings, 300-500X200mm | m | 21
BILL No: 04 - MASONRY AND PLASTERING
TOTAL OF BILL No: 04 - Carried over to summary
BILL No: 05
ROOFING
5.1 | General
(a) Rates shall include for: fair edges, dressing over angel fillets, turning into grooves, all other labors, circular edges, nails, screws and other fixings and laps.
(b) Rates shall include to apply Wood preservative to all the surface of timbers (Roof structure).
(b) Rates shall include to remove existing end cap, fascia board and necessary roofing sheets and necessary works to connect new roof to existing roof.
5.2 | Roof Coverings
1 | Roofing sheets: Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick - Aqua marine or equivalent for Main building and connection area. | m² | 316.22
5.3 | Capping and Flashings
1 | Ridge Capping as per drawing: Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick- Aqua marine or equivalent | m | 17.65
2 | Flashing as per drawing: Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick- Aqua marine or equivalent | m | 15.4
3 | End cap (Roof hips): Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick- Aqua marine or equivalent | m | 36.4
5.4 | Gutter
(a) MSP Color bond flat sheet gutter 200X200mm, Total coated thickness minimum 0.47mm thick, including framing, and supports, straps, brackets, clips, stop ends, overflow, downpipe outlets, mesh flashings and all fixings and fastenings.
1 | GUTTER: Blue scope steel international MSP- Aqua marine or equivalent for new building | m | 35.3
5.5 | Down Pipes
1 | 75 mm dia uPVC down pipes including bends, junctions, straps, brackets, clips, roof drain strainer and all fixings. | m | 35.63
5.7 | Roof Structure
1 | (a) Rates shall include for: all labor in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails and screws. (b) Rates includes to applying solignam wood preservative oil to all the surface of roof structure. (c) Rates include to fixing galvanized bolt, washers, nuts and 3mm thick MS gusset plates as show on the drawings.
1 | Timber rafters 50 X 100mm ( Rates must include fixing of Gusset plates, and 12mm dia bolts as per the drawings) | m | 308.16
2 | Timber purling 50 X 50mm | m | 425
3 | Facia board, 18mm thick SHERA board 18 X 250mm | m | 73.7
4 | Applying Solignum wood preservative or equivalent for all roof structure | item | 1
5.8 | Fabrication and fixing of GI Truss
1 | (a) Rates shall include for: all fabrication work, welding, marking, drilling, for bolts including those securing timbers, steel plates, bolts, nuts and any type of washer, riveted work, counter sinking and tapping for bolts or machine screws.
(b) Rates shall include for all painting and finished as specified. Quality of paint should be high quality and primer and finish coat to be applied for all steel pipe.
(c)Rates shall include for fabrication and erection and temporary supports and fixing in to position.
1 | Fabrication and fixing of GI Truss as per drawing. | m | 30.5
5.9 | Roof Insulation
1 | 25mm thick Mineral wool installation with both side reflective foil on Fixed to underside of roofing with 12.5X12.5mm plastic mesh, Connection and edges of the foil to be sealed properly with a approved tape approved from consultant. | m² | 316.22
5.1 | Roof Insulation
Supply and Complete installation of Furniture's For Health center use.
1 | Office Table with drawer, 1200mm, | No | 2
2 | Secretary chair , high back. | No | 6
3 | Secretary chair , low back. | No | 8
4 | Supply and installation of 3 seater Airport Bench set, Armrest/Leg/bracket: Die-casting molding of high strength aluminum alloy. Seat: Numerical control hydraulic molding of high quality cold rolling steel plate. Sponge: Cold consolidation and foam-forming of high density and super soft PU. Beam: metal tube with a diamond shape. Coating: Electrostatic coating after Rust-proof treatment, electroplated polishing. | No | 4
5.11 | Shelves
1 | Design and Fabrication of Wooden shelves at Store Store room, length of Shelf is 1.2M, Width is 0.4m and heigh is 2M, 18mm thick Plywood with both side paint to be used. Frame with 4 shelf, | Item | 8
BILL No: 05 - ROOFING
TOTAL OF BILL No: 05 - Carried over to summary
BILL N0: 06
DOORS AND WINDOWS
6.1 | General
Aluminum Doors and windows, Fabricate and fix in position the aluminum doors and window frame - aluminum doors and window (white powder coated, 60-80 micron, 1.5mm profile thickness) using recommended material with specified fixtures as shown in approved working drawings and installation should be as per technical specifications. Rates shall include for locks, latches, closures, push plates, pull handles, bolts, kick plates hinges, screws, washer and all door and window hardware and these materials should be of ss steel according to drawing and of superior quality.
(a) All door and window frames and panels shall be as specified in the drawing and timber boarder to be fixed all timber doors.
(Profiles to be chosen by client, Thickess of aluminium profile must be minimum 2mm thick).
6.2 | Door / Windows units
1 | D1, Minimum 80 Micron Aluminum, Dark sandy grey powder coated Door 2600X1800mm with panels as per drawings at Existing Health center, Rates must includes to remove existing main Entrance door at health center and install new door. | no | 1
2 | D2, Minimum 80 Micron Aluminum, Dark sandy grey powder coated Door 2150X1950mm with panels as per drawings. | no | 1
3 | D3, Timber Door 2150X1350mm with panels as per drawings. With timber border on both side of door leaf. | no | 3
4 | D4, Timber Door 2150X950mm with panels as per drawings. With timber border on both side of door leaf. | no | 7
5 | D5, Minimum 80 Micron Aluminum, Dark sandy grey powder coated Door 2150X900mm with panels as per drawings. | no | 8
6 | W1, Minimum 80 Micron Aluminum, Dark sandy grey powder coated window 1700x1300mm with panels as per drawing. | no | 2
7 | W2, Minimum 80 Micron Aluminum, Dark sandy grey powder coated window 1700x675mm with panels as per drawings. | no | 4
8 | V1, Minimum 80 Micron Aluminum, Dark sandy grey powder coated window 500x675mm with panels as per drawings. | no | 8
9 | V1, Minimum 80 Micron Aluminum, Dark sandy grey powder coated window 500x675mm with panels as per drawings. Garage area V1 must fix safety grill. | no | 1
6.4 | Vertical Blinds
Supply and installation of Vertical Blinds for following windows, quality of vertical blinds should be high quality sun protected , Rates should be complete installation of Vertical blinds with railing and ect..
1 | W1 windows , size of finished blinds should be 1.7m height, X1.3meter width. | No | 2
2 | W2 windows , size of finished blinds should be 1.7m height, X0.675 meter width. | No | 4
6.5 | BED SIDE CURTAINS
Supply and complete installation of top quality Hospital grade bed side curtain including railing/Track. Length of rail/track is 6870mm, and height of curtain would be 2.4 meter. Aluminium hollow section to be use If extender to the rail level.
1 | Ward 1, Private / Critical room , Consultation room and Procedure room, | Item | 6
6.6 | Nurse Station counter
1 | Design and Fabrication of Nurse station counter as per Floor plan, Fabrication of counter to be timber and appropriate thick plywood with PVC fomica. Length of Registration counter is 3 Meter with 2 drawer. | No | 1
2 | Design and Fabrication of Reception Counter counter as per Floor plan, Fabrication of counter to be timber and appropriate thick plywood with PVC fomica. Length of Registration counter is 3 Meter with 2 drawer. | No | 1
BILL N0: 06 - DOORS AND WINDOWS
TOTAL OF BILL No: 06 - Carried over to summary
BILL N0: 07
TILING
7.1 | General
Prepare surface for approved bedding tiles with reach bedding materials as per the technical specifications & approved working drawings, fix tiles with ct grout in a precise manner to maintain correct alignment, applying tile grout and wiping any excess grout to ensure the required standards of finished works. Rates shall include for: fixing, bedding, grouting, and pointing materials; making good around pipes, sanitary fixtures, and similar; cleaning down and polishing any other similar works to ensure the required finish. All tiles shall be skid resistant full body homogeneous Matt finish tiles or equivalent.
7.2 | Floor finish
7.2.1 | 600x600 skid resistant dfull body homogeneous tiles, matt finish floor tiles,
1 | General floor tiling | m² | 225.44
2 | Toilet floor tiling, With Water proofing membrane, approved by the Client. | m² | 25.29
3 | Removal of existing floor tiles, repair the floor and lay new tiles at existing wards area with toilet. | m² | 22.984
7.3 | Wall finish
7.3.1 | 300x600 mm full body homogeneous wall tile,
1 | Nurse Station toilet 2.4 meter from floor finish level | m² | 19.49
2 | Ward 1, 1.8 meter from floor finish level | m² | 21.21
3 | Ward 1 toilet 2.4 meter from floor finish level | m² | 22.15
4 | Ward 1 washing area 2.4 meter from floor finish level | m² | 16.51
7 | Dirty Utility 2.4 meter from floor finish level | m² | 23.83
10 | Private/Critical room 2.4 meter from floor finish level | m² | 55.73
11 | Private/Critical room Toilet 2.4 meter from floor finish level | m² | 22.15
12 | Labour room 2.4 meter from floor finish level | m² | 51.83
13 | Labour room Toilet 2.4 meter from floor finish level | m² | 20.44
14 | Tile skirting 150mm height, for all internal walls, Masonary walls and Partitions walls | Item | 1
BILL No: 7 - TILING
TOTAL OF BILL No: 7 - Carried over to summary
BILL No: 8
CEILINGS
8.1 | Interior Ceilings
Interior ceiling consist of 50X50mm Timber frame @ 1200mm c/c vertical and 600mm c/c horizontal frame with 10mm thick Gypsum board suspended ceiling, including framing beading nails and screws as per manufactures instruction. All the timber must be treated or applied wood preservative oil before fixing the Gypsum board.
1 | Ground floor for General area. | m² | 279.13
2 | Removal of existing ceiling and install 2 level new ceiling with LED strip at the existing wards area with toilet. | m² | 22.984
8.2 | Exterior Ceilings
Exterior ceiling consist of 6mm thick Shera board suspended ceiling, including framing beading nails and screws. Grid of the frame to be 600 X 600 with timber supports to roof structure at every 1200 mm on the main entrance ceiling & 600X900 mm at eaves of roof ceiling, timber framing and supports shall 50 x 50mm size shall be seasoned red meranti timber as per given drawing.
1 | Ground floor | m² | 52
BILL N0: 8 CEILINGS
TOTAL OF BILL No:8 - Carried over to summary
BILL No: 9
PAINTING
9.1 | General
Exterior wall shall be of 1 coat of oil based textured paint and 2 coats of Kansani weather bond paint ( oil based ) over 1 coat of oil based sealer ( white) or equivalent (according to technical specifications or approved drawings). Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window and including soffits and sides of beams.
Interior wall shall be of 2-3 coats over 1 coat of water based sealer. Rates includes Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint, Kansani or equivalent as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window and including soffits and sides of beams.
Exterior & Exterior Ceiling (interior and exterior) shall be of 2 coats of (wood paint over 1 coat of wood primer, Kansani or equivalent. Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for the provision and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and or masking floors fittings and similar work removing and replacing door window furniture.
All painting work shall be carried in accordance with the Specifications
9.2 | Wall painting
9.2.1 | External painting 1 coat of wall sealer, 2 coats of paints ( all coats to be oil based and external paint).
Internal Painting 1 coat of wall sealer & 2 coats of paints, Emulsion paint putty finish system on plastered and concrete surfaces of internal walls.
1 | Ground floor interior and exterior serface painting ( Masonry walls) | m² | 466
2 | Internal Painting 1 coat of wall sealer & 2 coats of paints, Emulsion paint putty finish all the surfaces of internal Partition walls and AC boxing | m² | 198
3 | Painting of new waiting area of existing health center | m² | 98
9.3 | Interior Ceiling painting
9.3.1 | Emulsion paint putty finish on concrete slab and beams, plywood / cement fiber board of all internal surfaces. 1 coat of primer & 2 coats of paints.
1 | Emulsion putty paint finish | m² | 302.13
9.4 | Exterior ceiling painting
1 | Exterior Ceiling painting as per specification given. | m² | 52
BILL No: 9 - PAINTING
TOTAL OF BILL No: 9 - Carried over to summary
BILL No: 10
ELECTRICAL INSTALLATIONS
10.1 | General
(a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories
(b) Rates for work in trench shall include for: excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers, warning tape and disposal of surplus spoil
(c) Rates shall include for electrical conduits, fittings, equipment and similar all fixings to various building surfaces
(d) Each Light/ light fixture and its switch is measured as one point; similarly each fan or each socket outlet is measured as one point;
(e) Rates shall include for supply and complete installation
10.2 | Mains connection
1 | Main connection: Rates shall include screws, nails, bolts, nuts, standard cable, fixing or supporting clips, brackets, straps, rivets, plugs, and all incidental accessories. Rates shall include electrical conduits, fittings, equipment, and similar items. Three - PHASE CABLE WIRING TO D-BOARD: All necessary work in trench shall include excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers warning tape, and disposal of surplus soil supply and laying of the cable in according to Maldives electricity bureau. (16mm2 4-Core Cable, approved by respective Authorities, GI pipe, warning tape), the contractor has to measure cable length from the site. The main cable must be connected to the existing health center. The contractor must inspect the site and Upgrade the Main distribution board if necessary to connect the Health center as well as the extension Building as per Fenaka requirements. | no | 1
2 | 3Phase connection for Health Center Building, Rates must include laying 16mm2 4-Core Cable, upgrading the Distribution bord, 3 phase Digital house meter, and other necessary materials with labor charges. | Item | 1
10.3 | Electrical Boards
1 | A three-phase electrical distribution board (wall embedded), Supply, and complete installation of D-Boards. Rates Shall include all required Brackets and other electrical appliances per drawings and Maldivian Regulations. For Lights. 5 Lights or Fan for one Circuit. For sockets, 13amp 2 sockets for one circuit, 15amp socket for one circuit.All the ELCB, MCB, and Circuits as well as the D board must be Henger, Legrand, ABB or Equivalent. | no | 2
10.4 | Electrical wiring
Three phase Electrical wiring with copper conductor Keani cable in conduits in walls and in casing on soffits of slab as specified to:
1 | Wiring with 2.5 mm² cable to 1X13amp Power points | points | 29
2 | Wiring with 2.5 mm² cable to 2X13amp Power points | points | 39
3 | Wiring with 6 mm² cable to 1 x 15 Amp Power points | points | 3
4 | Wiring with 6 mm² cable to 1 x 15 Amp Power points (for AC) | points | 9
5 | Wiring with 2.5 mm² cable to lights and fan | points | 76
10.5 | Lighting / Fan
1 | Ceiling diffusing embedded down light 200mm dia with 21W LED bulb, (Philips), Cool day light, (not crystal light or not Stellar bright) Total lumen 2300 or equivalent, | no | 58
2 | Ceiling Fan 900mm dia, Usha or equivalent | no | 10
3 | Whether proof wall mount light with ( Glass cover) 13W LED bulb, (Philips) E27, warm white, Total lumen 1400, | no | 8
4 | LED Emergency light ( 2 hours Battery charge) | no | 9
5 | Dimmable light with cover for ward area and private room. | no | 3
6 | 300mm Dia, wall fan at Dirty utility room | Item | 1
10.6 | Socket outlets
(a) All socket outlets shall be "Legrand" or equivalent.
1 | 1x13Amp wall Socket outlet, | no | 29
2 | 2x13Amp wall Socket outlet, | no | 39
3 | 1x15Amp wall socket outlet, | no | 3
4 | 1x15Amp wall socket outlet, for AC | no | 9
10.7 | Light switches
(a) All light switches shall be "Legrand" or equivalent. Each light should be control by one switch.
1 | One gang switch | no | 21
2 | Two gang switch | no | 10
3 | Three gang switch | no | 9
4 | Fan Controller | no | 10
5 | Out door photo cell switch | no | 3
10.8 | Computer Network
Design, Supply and Complete Installation of computer networking, including CAT6 Cabling, Sockets and double layer switches, Allow for the provision of a completed and detailed set of shop drawings
1 | Completion of Data Network points including face plate, face plate must be "Legrand" or equivalent. | No | 8
2 | Supply and complete installation of 24 port, VOIP, Double layer Manageable network switch D-Link or equivalent and connect to the Health Center network. | No | 1
3 | Supply and complete installation of Computer system as per specifications | No | 5
4 | Supply and complete installation of IP Telephone ( 4 phone at Extension and 4 Phone at existing Health center, Reception, Nurse station, Public Health Unit, Counsellinig room and Consultation room). | No | 8
5 | Supplying of Surface Pro for Business, Copilot+ PC, 13-inch ¦ Intel Intel® Core™ Ultra 7 processor (Series 2), with OLED display, Platinum, 32GB RAM, 512GB SSD Surface Pro 13-inch Keyboard with Slim Pen for Business with Slim Pen For PMU use. | No | 2
6 | Supply and complete installation of 65" QLED TV, LG or Equivalent at meting room. Any cast or chrome cast must support. | No | 1
10.9 | Earthing
Earth pit with resistance less than 2 ohms
3/4 earth rods must be used and must have clamps at the end
Earth pit should be covered junction with cover.
1 | Completion of earth pit with earthing cable and completion of earthing as per the above requirements. | Item | 1
10.1 | Fire Fighting
1 | CO2 Extinguisher | Item | 4
2 | H2O Extinguisher | Item | 4
10.11 | Lightening Protection System
1 | Design, supply, and Complete installation of Erco, Eritech or equivalent lightening Protection System to cover the whole building as per local regulations (Rate shall include for all fixing of the system and down conductor to earthing) Coverage of lightning protection should be minimum 100 Meter Radius. Price also include to install GI pipe post. GI pipe must be 75mm dia and minimum thickness is 2mm thick. | Item | 1
10.12 | SOLAR PV SYSTEM
1 | Design supply and complete installation on 10KW Solar PV system. Rates includes to complete the system and connect to the grid with net metering as per specification. ( junction box specs, Solar AC&DC cable specs, solar bracket specs, inverter specs & solar panel specs). | Item | 1
2 | We propose the supply of a 30KW Bluesun Stackable Lithium Battery High Voltage Series for the Energy Storage System, along with the necessary gear to integrate it with the existing Bluesun solar Grid PV system for PMU use. Delivery location is MoH. | Item | 4
10.13 | MEDICAL OXYGEN FOR ALL BEDS
GENERAL
a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
b) Rates shall include for: Design, supply and install according to Health facility operators’ demand/specifications. screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
10.13.1 | OXYGEN DELIVERY SYSTEM
Design supply and complete installation of Piped and tested oxygen delivery system from the Oxygen bank to the Bed as per Specifications and manufactures guidelines, instructions. Oxygen bank, capacity to connect minimum 5 jumbo cylinder. System to be insttaled as per manufactures instructions. The system is to be installed according to the manufacturer's instructions. (The location of Oxygen bank is to be at the garage area.) Medical Gas System to be design and instlled as per the HTM Standard. List of specialist Equipments – Medical gas system According to HTM Standard 1. Medical Gas Distribution System 2. AVSU 3. Lockable Line Valves 4. Alarm Systems 5. Medical Gas Automatic Manifold System 6. Medical Gas Reserve Manual Manifold System 7. Combined Medical & Surgical Air System 8. Medical Vacuum System 9. AGS System 10. Wall Outlets for Oxygen
1 | Ward 1 | Item | 4
2 | Private room | Item | 1
3 | Labour room | Item | 1
BILL No: 10 - ELECTRICAL INSTALLATIONS
TOTAL OF BILL No: 10 - Carried over to summary
BILL No: 11
HYDRAULICS & DRAINAGE
11.1 | Hydraulics
11.1.1 | General
(a) Rates shall include for excavation, laying pipes and backfilling trenches, maintaining faces of drainpipe trenches and pits, backfilling, disposal of surplus soil, bends, junctions, reducers, expansion joints brackets, joints, straps, hangers, screws, nails and fixing complete, and all joints and other incidental material, All Pipes and fittings area high pressure uPVC pipes
fixing complete, including cutting and forming holes; excavating, laying pipes and backfilling trenches.
(b) All pipe work shall be uPVC.
11.1.2 | Fresh water supply pipe work
1 | Completion of pipe works and Connect Fresh water supply pipe work to Fresh water network installed at hospital. | Item | 1
11.1.3 | Sanitary fixtures & accessories
Sanitary fixtures & Accessories: Sanitary fixtures complete including brackets, flush pipes, valves, overflows, plugs and washers, as specified.
1 | Water closet (American standard, Neo Modern, Anti bacterial type) or equivalent, (dual top flush) | no | 5
2 | Wash basin with pedestal (American Standard) or equivalent | no | 5
3 | Water tap for wash basin , ( Cotto) or equivalent | no | 5
4 | Muslim Shower with Stop valve, ( Cotto) or equivalent | no | 5
5 | Floor waste with SS gully trap, All toilets, Laundary and Dirty utility | no | 8
6 | Stop Valves, ( Cotto) or equivalent | no | 14
7 | Head shower with Head shower Valve, ( Cotto) or equivalent | no | 3
8 | Hand shower with Hand shower Valve, ( Cotto) or equivalent | no | 3
7 | Wall cabinet ( Mirror and towel bar only) Cotto and equivalent | no | 5
8 | Water tap, outside of Garage area with 10 Meter high quality pipe 12.5mm dia. | no | 1
9 | Water tap for washing Machine. | no | 1
10 | Supply and complete installation of Hitachi Front Load Machine, BD-D100XGV 3C MAG washing machine, minimum capacity must be 10KG. | no | 1
11 | SS hand rails for Ward 1, Private room. Labour room Toilet as per international standard. | Item | 3
12 | Supply and complete installation of PANASONIC Magic Health Shower Heater DH- 3KD1 or equivalent at ward and Private room and Labour room toilet. | Item | 3
11.2 | Drainage
11.2.1 | General
(a) Rates shall include for: excavation, maintaining faces of drain pipe trenches and pits, backfilling, disposal of surplus spoil; bends, junctions, reducers, expansion joints and all joints and other incidental materials.
(b) All pipe work shall be UPVC
1 | Constructing Concrete Inspection Chamber of required size with all provisions to connect pipelines as per drawing. | Item | 4
11.3 | Pipe work
1 | Completion of pipe works and Connect Waste disposal pipe 75mm dia to Sewer network installed at existing system. | Item | 1
2 | Completion of pipe works and Connect Sewers pipe 100mm dia UPVC to Sewer network installed at existing system. Rates includes to install inspection chamber as per consultants instructions. | Item | 1
BILL No: 11 - HYDRAULICS & DRAINAGE
TOTAL OF BILL No: 11 - Carried over to summary
BILL No: 12
AIR CONDITIONING SYSTEM
12.1 | General
(a) Rates shall include for detail design, supply and complete installation of A/C units pipework, insulation, fixings, electrical wiring, drain pipes etc.
(b) The Contractor shall provide detailed and complete set of shop drawings
c) The contractor shall submit shop drawings of AC and Exhaust System. The capacity shall be determined by the contractor.
d) Rate shall include complete installation of indoor units and outdoor units.
12.2 | Air Condition
12.2.1 | Design, supply and complete installation of indoor and out door unit, All AC unit is DAIKIN or equivalent (INVERTER TYPE).
The whole of the liquid and suction refrigerant lines including all fittings, valves etc. shall be insulated with 25mm thick insulation for all copper sizes. Insulation shall be closed cell elastomeric nitrile rubber.
Protection of exposed Refrigerant Pipe Insulation: To protect nitrile rubber of exposed piping from degrading due ultra violet rays & atmospheric conditions, it shall be covered polychelid coating with at least two coats of resin and hardener (Make-Polybond /Paramount Polytreat). Fiberglass tape shall be helically wound & painted with two coats of resin with hardener to give smooth & plain finish.
The proposed outdoor or outdoor set specifications should detail Energy Efficiency Ratio (EER) kw/kw not less than 4.5kw
The Outdoor Unit Shall be Factory assembled with Weather Proof casing, constructed from Heavy Gauge Mild Steel Panels and coated with Anti Corrosive Epoxy resin finish. The unit should be completely factory wired and tested and shall be fitted with all necessary controls and switch gear.
All outdoor units needs to have aluminum fins with 105+2 μm thickness, with special Anti corrosive coating of 1.3 ± 0. 35 μm thickness and an outside Hydrophilic layer coating of 0.35 ± 0. 07 μm thickness.
All outdoor units shall be equipped with high efficiency optimized heat exchangers with variable heat exchanger circuits
All the outdoor unit must be fixed back side of the Building.
AC to be install Following rooms, all the indoor unit should be spilt type.
1 | Ward area, 18,000 BTU spilt type wall mount air conditioner (with remote) Hitachi, LG or equivalent. | Item | 2
2 | Nurse station with corridor area, 18,000 BTU spilt type wall mount air conditioner (with remote) Hitachi, LG or equivalent. | Item | 2
3 | Labour room, 24,000 BTU spilt type Ceiling cassette air conditioner (with remote) Hitachi, LG or equivalent. | Item | 1
4 | General Store, 18,000 BTU spilt type wall mount air conditioner, Hitachi, LG or equivalent. | Item | 1
5 | Private / Critical Room, 36,000 BTU spilt type wall mount air conditioner, Hitachi, LG or equivalent. | Item | 1
6 | Medical store with Medical preparation room. 18,000 BTU spilt type wall mount air conditioner, Hitachi, LG or equivalent. | Item | 1
7 | Medical Store, 18,000 BTU spilt type wall mount air conditioner, Hitachi, LG or equivalent. | Item | 1
8 | Existing OPD Area, 36000BTU spilt type wall mount air conditioner (with remote) Hitachi, LG or equivalent or equivalent.. Rates includes to install additional power point to connect AC units. | Item | 2
9 | New PHU, 24000BTU spilt type wall mount air conditioner (with remote) Hitachi, LG or equivalent or equivalent. | Item | 1
12.4 | Air Curtain
Supply and Complete installation of Air curtain.
1 | Supply and Complete installation on KDK (10ESK ) air curtain with Sensor, 900mm length at Exit door. Rates also includes to electric connection. | Item | 2
BILL No: 12 -AIR CONDITIONING SYSTEM
TOTAL OF BILL No: 12 - Carried over to summary
BILL No:13
TENDERER'S ADJUSTMENTS
13 | Any adjustments that the contractor may consider necessary should be written below and on similar continuation sheets if required, and the net amount of the adjustments is to be carried to the summary.
(a) If there are discrepancies between BOQ and Drawings, the Contractor must include them in the Addition/Ommision Bill. If the contractor does not include the Addition/Ommision bill, the contractor must proceed with the works without any cost.
(b) Provide detail description of work items under each bill and insert extra pages if required.
13.2 | Additions
1 | PRELIMINARIES, Bill no. 01
2 | GROUND WORKS, Bill no. 02
3 | CONCRETE, Bill no. 03
4 | MASONRY AND PLASTERING, Bill no. 04
5 | METAL WORKS, Bill no. 05
6 | DOORS AND WINDOWS, Bill no. 06
7 | TILING, Bill no. 07
8 | CEILINGS, Bill no. 08
9 | PAINTING, Bill no. 09
10 | HYDRAULICS & DRAINAGE, Bill no. 10
11 | ELECTRICAL INSTALLATIONS, Bill no. 11
12 | AIR CONDITIONING SYSTEM, Bill no. 12
13 | TENDERER'S ADJUSTMENTS, Bill no. 13
ADDITIONS TOTAL
13.3 | Omissions
1 | PRELIMINARIES, Bill no. 01
2 | GROUND WORKS, Bill no. 02
3 | CONCRETE, Bill no. 03
4 | MASONRY AND PLASTERING, Bill no. 04
5 | METAL WORKS, Bill no. 05
6 | DOORS AND WINDOWS, Bill no. 06
7 | TILING, Bill no. 07
8 | CEILINGS, Bill no. 08
9 | PAINTING, Bill no. 09
10 | HYDRAULICS & DRAINAGE, Bill no. 10
11 | ELECTRICAL INSTALLATIONS, Bill no. 11
12 | AIR CONDITIONING SYSTEM, Bill no. 12
13 | TENDERER'S ADJUSTMENTS, Bill no. 13
OMISSIONS TOTAL
BILL No: 13 - TENDERER'S ADJUSTMENTS
TOTAL OF BILL No: 13 - Carried over to summary

## Boundary summary
SUMMARY OF BILLS OF QUANTITIES
CONSTRUCTION OF BOUNDARY WALL AT TH. BURUNI HEALTH CENTER
Bill No | Description |  | Amount
1 | PRELIMINARIES | Bill no. 01
2 | GROUND WORKS | Bill no. 02
3 | CONCRETE | Bill no. 03
4 | MASONRY AND PLASTERING | Bill no. 04
5 | PAINTING | Bill no. 05
6 | METAL WORKS | Bill no. 06
7 | TENDERER'S ADJUSTMENTS | Bill no. 07
Sub total
GST 8%
GRAND TOTAL carried to form of bid

## Boundary wall
BILL OF QUANTITIES (REVISED)
CONSTRUCTION OF BOUNDARY WALL AT B. FEHENDHOO HEALTH CENTER
B. FEHENDHOO ISLAND
Item | Description | Unit | Quantity | Rate/ Unit | Rate/ Unit | Total Unit Rate | Amount
|  |  |  | Material | Labour | Rates per Units
BILL No: 01
PRELIMINARIES
1.1 | General Notes
(1) | Abbreviations
m - meter
No - numbers
m³ - cubic meter
m² - square meter
Lm - Linear meter
KG - Kilograms
incl - including
mm - millimeter
dia - diameter
SS - Stainless Steel
GI - Galvanized Iron
1.2 | Site Clearing
1 | Includes clearing of all trees and bushes complete with stems, roots Flooring and the reimbursement fees if applicable. demolition and celening of debris of 86 meter of existing boundary wall, The contractor is advised to survey the construction site and ensure that all necessary works for site clearing are included and on completion of works. Rates must includes to remove existing flooring and clean the debris. | Item | 1
BILL No: 01 PRELIMINARIES
TOTAL OF BILL No: 01 - Carried over to summary
BILL No: 02
GROUND WORKS
2.1 | General
(a) Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, consolidating and disposing surplus soil.
2.2 | Excavation
Excavation shall be carried out in all type of materials and by whatever means are necessary accurately to the lines and levels shown in the approved drawing. No blasting of any kind will be permitted. Excavation for foundations and will include timbering of soil faces and dewatering. Excavation quantities are measured to the faces of concrete members. Rates shall include for dewatering, leveling, grading, trimming compacting to faces of excavation, keeping sides plumb, backfilling, consolidating and disposing surplus soil and include for all additional excavation required to place the formwork / shuttering and dewatering the trench for the required days also back filling for necessary areas.
1 | Excavation for Foundation Beams for Boundary wall | m³ | 15.54
2 | Excavation for Footings at garage area. | m³ | 0.24
2 | Backfilling of Garage area, 200mm fromn ground level. | m³ | 4.54
2.3 | Damp Proof Membrane
Cutting and laying in position heavy duty polythene sheets of gauge 500 (not less than 1.5mm thick). Rates shall include for: dressing around and sealing to all penetrations. Apply slurry type waterproofing to all surfaces of concrete below ground level in accordance with manufacturer's instructions.
1 | Damp proof membrane above lean concrete, | m² | 20.71
2 | Bituminous application to sides of foundation beams. | m² | 72.5
3 | Damp proof membrane below floor slab at garage area | m² | 22.72
BILL No: 02 - GROUND WORKS
TOTAL OF BILL No: 02 - Carried over to summary
BILL No: 03
CONCRETE
3.1 | General
Rates shall include for cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wire and other supports, laps and wastage, all reinforcement bars except 6 mm dia bars shall be of deformed high strength bars. 6 mm bar shall be round mild steel bars. Binding wire shall be of 1.6 mm or 1.4 mm soft iron wire. Reinforcement bars shall be cleaned before use i.e. should be free from rust, oil, din, or other coatings that reduces bonds, all reinforced bars and binding wires shall be stored under cover of at least 450 mm above the ground, cutting and bending according to approved manner & the approved working drawing, placing and fixing in position and binding should be as per the approved working drawing, laps in the bars shall be staggered, concrete cover for reinforcement shall not less than 50 mm for substructure, 40 mm for columns & side beams and not more than 30 mm for slab and beam bottoms.
3.2 | Lean Concrete
Lean concrete shall be 50mm thick & mix ratio shall be 1:3:6 by dry volume. Lean concrete placed at bottom of footing and foundation beam and below plinth for protection according to line and length mentioned in the approved drawing. Quantity measured to the edges of concrete foundation members. Rate shall include of placing any formwork where necessary, batching, mixing, casting in all required items pouring & compacting and curing for 3 days and removal of any formwork include for provision casting of required items & finishing after removal of formwork and additional concrete required to confirm to structural and excavated tolerances and rates shall include supply of all required works
1 | Foundation Beams | m³ | 1.29
2 | Footings, 350x350X400mm at garage area with PVC pipe as per drawings. | m³ | 0.15
3 | RCC Ground Slab 100 mm thick, (Garage and ramp area) rates includes to R10@150 B/W. | m³ | 2.5
3.3 | Reinforced Concrete
3.3.1 | Foundations
1 | Foundation Beam, FB 200x250mm | m³ | 5.18
2 | Concrete columns, 200 x 200mm | m³ | 1.56
3 | Concrete columns, 250 x 250mm (gate column) | m³ | 0.33
3.3.2 | Top Beam
1 | Top beam, 150x150mm | m³ | 2.15
2 | Mass concrete wall capping as well as column capping as per the drawings. | m | 103.57
3.3.3 | Drive way paving
1 | Paving ambulance way as per drawing. Rates include erecting Concrete edge blocks ( 300mm below ground level and 100mm from floor slab on both sides of ambulance way), backfilling, compacting, and laying 120mm thick RC slab, R6 @150mm c/c (BW), Ambulance way to be paved from Portico to the Gates. Starting point of the ambulance way from the roadside is +0mm and the Finishing to the portico floor finish level. Rates must include demolishing and cleaning debris on existing slopes on both sides of the portico. | m³ | 7.06
2 | 150mm wide Mass concrete curb stone with lean as per drawing, the height of curb stone will vary as per the slope. | m | 22
3.4 | Formwork
(a) Rates shall include for all necessary boarding, supports, erecting, framing, temporary cambering, cutting, perforations for reinforcing bars, bolts, straps, ties, hangers, pipes and removal of formwork. All materials such as plywood, shutter oils and other items and transportation to work place and secure the formwork in highly precise manner guaranteeing straight and smooth concrete edges. Cutting, fixing, bracing and oiling according to line and length as per approved working drawings removal of it after concrete has set without damaging the concrete faces.
3.4.1 | Foundations
1 | Foundation Beam, FB 200x250mm, ( 50% of form work), same form work to be use balance 50% Foundation. | m² | 25.89
2 | Columns, 200 x 200mm, ( 50% of form work), same form work to be use balance 50% column. | m² | 15.6
3 | Columns, 250 x 250mm, ( 50% of form work), same form work to be use balance 50% column. | m² | 1.28
4 | Top beam, 150x150mm, ( 50% of form work), same form work to be use balance 50% of top beam. | m³ | 14.34
3.5 | Reinforcement
GENERAL : Rates shall include for cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wire and other supports, laps and wastage, all reinforcement bars except 6 mm dia bars shall be of deformed high strength bars. 6 mm bar shall be round mild steel bars. Binding wire shall be of 1.6 mm or 1.4 mm soft iron wire. Reinforcement bars shall be cleaned before use i.e. should be free from rust, oil, din, or other coatings that reduces bonds, all reinforced bars and binding wires shall be stored under cover of at least 450 mm above the ground, cutting and bending according to approved manner & the approved working drawing, placing and fixing in position and binding should be as per the approved working drawing, laps in the bars shall be staggered, concrete cover for reinforcement shall not less than 50 mm for substructure, 40 mm for columns & side beams and not more than 30 mm for slab and beam bottoms.
(b) All reinforcing bars shall be high strength bars.
3.5.1 | Foundation
1 | Steel deformed bars, 12mm dia x 6m | Bars | 79
2 | Steel ring bars, 6mm dia x 6m | Bars | 69
3.5.2 | Columns (200X200mm)
1 | Steel deformed bars, 12mm dia x 6m | Bars | 26
2 | Steel ring bars, 6mm dia x 6m | Bars | 25
3.5.3 | Columns (250X250mm)
1 | Steel deformed bars, 12mm dia x 6m | Bars | 4
2 | Steel ring bars, 6mm dia x 6m | Bars | 3
3.5.4 | Top beam
1 | Steel deformed bars, 10mm dia x 6m | Bars | 79
2 | Steel ring bars, 6mm dia x 6m | Bars | 58
BILL No: 03 - CONCRETE WORKS
TOTAL OF BILL No: 03 - Carried over to summary
BILL No: 04
MASONRY AND PLASTERING
4.1 | General
Rates shall include for: cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding frames or plates, building in joists, bearers or similar, temporary supports to openings, templates, reinforcement in walls and for all necessary making good. Bedding mortar (mixing ratio 1:4 i.e. cement: River sand) shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance. Masonry work shall be done with approved cement blocks (300X150X150) with no defects. Lay in line and length as per approved working drawing
floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding
Rates shall include for: 25mm groove lines on external surfaces as shown on the drawing.
Block Making (mixing ratio 1:4 i.e. cement: Local sand) shall be of OPC & local (salt free) sand shall be approved in grading & clean from any harmful substance.
4.2 | Cement block work
1 | 150mm Thick Hollow block Masonry wall | m² | 134.64
2 | Garage area side walls with 50mm thick lean | m² | 7.3
4.3 | Plastering
GENERAL: Interior and Exterior: Plaster All masonry wall have smooth finishing of 20 mm thick cement plastering with mix ratio 1:4 (i.e. cement: River sand), plastering material shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance. Plastic net should be provided wherever concrete surface and masonry meets, and cracks are unacceptable. Regular curing up to 7 days must be done
1 | Interior and Exterior and exterior plaster 18mm thick, including wall, columns ans capping. | m² | 269.28
2 | Garage area side walls | m² | 10.5
4.4 | Flag Post
1 | Supply and Complete installation of 75mm dia Flag post, length of flag post is minimum 5.9 Meter, Flag post must install minimum 10mm thick SS flang with SS bolts. Flag post to be fabricated in Marine grade SS pipe with 350X350X600mm concrete footings. | Item | 1
BILL No: 04 - MASONRY AND PLASTERING
TOTAL OF BILL No: 04 - Carried over to summary
BILL No: 5
PAINTING
5 | General
Exterior wall shall be of 1 coat of oil based textured (3mm flat head) paint and 2 coats of Kansani weather bond paint ( oil based ) over 1 coat of oil based sealer ( white) or equivalent (according to technical specifications or approved drawings). Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window and including soffits and sides of beams.
All painting work shall be carried in accordance with the Specifications
5.1 | Wall painting
1 | External painting 1 coat of wall sealer, 1 coat texture compound (3mm flat head) & 2 coats of paints ( all coats to be oil based and external paint). | m² | 294.88
BILL No: 5 - PAINTING
TOTAL OF BILL No: 5 - Carried over to summary
BILL No: 06
METAL WORKS
5.1 | General
(a) Rates shall include for: all fabrication work, welding, marking, drilling, for bolts including those securing timbers, steel plates, bolts, nuts and any type of washer, riveted work, counter sinking and tapping for bolts or machine screws. (b) Rates shall include for all painting and finished as specified. (c)Rates shall include for fabrication and erection and temporary supports and fixing in to position. (d) Rates also includes to paint high quality redoxcide at all the welded areas.
5.1 | Column
1 | 50mm Dia, GI pipe column 3.8Meter (L) with 6mm MS plate and 12mm GI bolt ( 1 nuts with washer for each bolt) , as per drawing for garage area. Pipe thickness must be Minimum 3mm. | Nos | 3
2 | 50mm Dia, GI pipe column 3.9Meter (L) with welding as per drawing for garage area. Pipe thickness must be Minimum 3mm. | Nos | 1
3 | 50mm Dia, GI pipe column 4.2Meter (L) with welding as per drawing for garage area. Pipe thickness must be Minimum 3mm. | Nos | 1
5.11 | Rafters
1 | 50mm Dia, GI pipe rafter with fixing plate and bolts as per drawings, length of rater is 3.98 meters, Pipe thickness must be Minimum 3mm. | Nos | 3
2 | 50mm Dia, GI pipe to connect rafters as per drawings, length of pipe is 6 meters, Pipe thickness must be Minimum 3mm. | Nos | 1
3 | 25X25 Dia, Hollow pipe purlins, | m | 40.5
5.11 | Garage wall cladding
1 | Roofing sheets: Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick - Aqua marine or equivalent for Main building and connection area. Rates should include the eve are of the existing roof. | m² | 27.7
2 | 25mm Dia, GI pipes as per drawings, Pipe thickness must be Minimum 3mm. | meters | 38
5.2 | Roof Coverings
Roofing sheets: Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick - Aqua marine or equivalent
1 | Garage area roof | m² | 27.06
5.3 | Gutter
(a) MSP Color bond flat sheet gutter 200X200mm, Total coated thickness minimum 0.47mm thick, including framing, and supports, straps, brackets, clips, stop ends, overflow, downpipe outlets, mesh flashings and all fixings and fastenings.
1 | GUTTER: Blue scope steel international MSP- Aqua marine or equivalent | m | 7.5
5.4 | Down Pipes
1 | 75 mm dia uPVC down pipes including bends, junctions, straps, brackets, clips, roof drain strainer and all fixings. | m | 10
9.2 | Electrical wiring
Three-phase Electrical wiring with copper conductor cable in conduits in walls and in the casing on soffits of the slab as specified to Rates must include connecting to existing D board and additional circuits to be installed.
1 | Wiring with 2.5 mm² cable to lights and fan | points | 3
2 | connection of existing D board and electric network. | Item | 1
9.3 | Lighting / Fan
1 | Whether proof wall mount light with 13W LED bulb, (Philips) E27, Cool day light, Total lumen 1400, for Portico area | no | 3
9.4 | Light switches
(a) All light switches shall be "Legrand" or equivalent. Each light should be control by one switch.
1 | Three gang switch | no | 1
2 | Out door photo cell switch | no | 1
BILL No: 05 - ROOFING
TOTAL OF BILL No: 05 - Carried over to summary
BILL No:6
TENDERER'S ADJUSTMENTS
Any adjustments that the contractor may consider necessary should be written below and on similar continuation sheets if required, and the net amount of the adjustments is to be carried to the summary.
(a) If there are discrepancies between BOQ and Drawings, the Contractor must include them in the Addition/Ommision Bill. If the contractor does not include the Addition/Ommision bill, the contractor must proceed with the works without any cost.
(b) Provide detail description of work items under each bill and insert extra pages if required.
6.1 | Additions
1 | PRELIMINARIES, Bill no. 01
2 | GROUND WORKS, Bill no. 02
3 | CONCRETE, Bill no. 03
4 | MASONRY AND PLASTERING, Bill no. 04
5 | PAINTING, Bill no. 08
ADDITIONS TOTAL
6.2 | Omissions
1 | PRELIMINARIES, Bill no. 01
2 | GROUND WORKS, Bill no. 02
3 | CONCRETE, Bill no. 03
4 | MASONRY AND PLASTERING, Bill no. 04
5 | PAINTING, Bill no. 08
OMISSIONS TOTAL
BILL No: 6 - TENDERER'S ADJUSTMENTS
TOTAL OF BILL No: 6 - Carried over to summary