Section 6 - Employer’s Requirements

Table of Contents

1	Scope of Supply of Plant and Services	5

1.1	General	5

1.2	Scope of work	6

2	Site Specifications	9

2.1	General	9

2.2	Logistic	9

2.3	Hybrid mini-grid systems and general behaviour	9

2.4	Other design characteristics	12

2.5	Summary of the characteristics of the BESS to be built	13

2.6	L06 F Nilandhoo island	14

2.7	A10 Dhidhoo island	17

3	Technical specifications	20

3.1	General	20

3.2	Battery Energy Storage System (BESS)	20

3.3	Civil and Mechanical requirements	29

3.4	Energy Management System – EMS	44

3.5	Utility compatibility	61

3.6	Earthing	66

3.7	Over voltage protection	67

3.8	Labelling, safety signs and notices	67

3.9	Noise and Radio Interference	69

3.10	Commissioning and Onsite Acceptance Tests	69

3.11	Documentation	72

3.12	Training Program	74

3.13	Ongoing O&M and troubleshooting support	75

3.14	O&M Service Requirements during the initial two-year operation	76

3.15	Detailed scope of Maintenance	77

3.16	Spare parts, consumables and special tools	79

4	Environmental, Health and Safety Management Requirement	80

5	Drawings	84

6	Certificates	85

6.1	Form of Completion Certificate	85

6.2	Form of Operational Acceptance Certificate	86

7	Change Orders	87

7.1	Change order procedure	87

7.2	Change Order Forms	88

8	Personnel Requirements	97

9	Equipment Requirements	98

Annex 1. Environmental Management Plan	99

LIST OF FIGURES

Table ‎1-1:List of islands for BESS & EMS with island code for Faafu Atoll	5

Table ‎1-2: List of islands for EMS with island code for Haa Alifu Atoll	5

Table ‎2-1 : Summary of BESS & EMS System to be installed in each atoll	13

Table ‎2-2 : L06 - Island identification and general data	14

Table ‎2-3 : L06 Diesel Generator currently installed	15

Table ‎2-4 : A10 - Island identification and general data	17

Table ‎2-5 : A10 - Diesel Generators currently installed	18

Table ‎3-1: PV Plant data to be sent to the central SCADA	59

Table ‎3-2: DG data to be sent to the central SCADA	60

Table ‎3-3: BESS data to be sent to the central SCADA	61

LIST OF TABLES

Figure ‎1-1 : Faafu aerial view with some selected islands	5

Figure ‎2-1: Simulation of energy distribution over 2 typical days (Type B: PV-Diesel-grid support battery)	11

Figure ‎2-2: Simulation of energy distribution over 2 typical days (Type C: PV-Diesel-grid forming battery)	11

Figure ‎2-3 : L06 – Map of island	14

Figure ‎2-4 : Single Line Diagram for Nilandhoo Island	16

Figure ‎2-5 : A10 - Map of island	17

Figure ‎2-6 Single Line Diagram for Dhidhoo Island	19

Figure ‎3-1 Potential installation sites for the BESS (red rectangle).	28

ABBREVIATIONS

| AC BESS | - - | Alternate Current Battery Energy Storage System |
| --- | --- | --- |
| CAPEX DC DG DOD | - - - - | Capital Expenditure. Direct Current Diesel Generators Depth Of Discharge |
| EMS FENAKA FOC | - - - | Energy Management System The Utility responsible for electricity, water and sanitation Fiber Optics Cable |
| PMU | - | Project Management Unit |
| GUI GRIDB MPP OEM PV | - - - - - | Graphical User Interface Grid Building Battery Inverter Maximum Power Point Original Equipment Manufacturer Photovoltaic |
| RE | - | Renewable Energy. |
| SCADA SLD SOC SWA SS THD UPS | - - - - - - - | Supervisory control and data acquisition Single Line Diagram State Of Charge Steel wire armoured Substation Total Harmonics Distortion Uninterruptible Power Supply |

WEIGHTS AND MEASURES

| kW | – | Kilowatt |
| --- | --- | --- |
| kWh | – | Kilowatt-hour |
| MW | – | Megawatt |

# Scope of Supply of Plant and Services

## General

The aim of the present tender is to implement a BESS (Battery Energy Storage System) and an EMS (Energy Management System) on one island located in Faafu atoll and one island located in Haa Alifu atoll, Maldives.

The specific islands for the BESS and EMS are listed in Table ‎1-1 and Table ‎1-2, respectively.

| Faafu Atoll |  |  |
| --- | --- | --- |
| Island Code | Island Name | Coordinates |
| L06 | F Nilandhoo | 03º03’ N 72º53’ E |

Table ‎1-1:List of islands for BESS & EMS with island code for Faafu Atoll

| Haa Alifu Atoll |  |  |
| --- | --- | --- |
| Island Code | Island Name | Coordinates |
| A10 | Ha Dhidhoo | 06º53’ N 73º6’ E |

Table ‎1-2: List of islands for EMS with island code for Haa Alifu Atoll

An aerial view of the islands are provided below:

| Figure ‎1-1 : Faafu aerial view with some selected islands | Figure 1-2: Haa Alifu aerial view with some selected islands |
| --- | --- |

## Scope of work

The scope of supply, works and services shall cover, but not limited to the following:

assessment of the site and site characteristics.

development, detailed design, engineering (including equipment specifications), coordination of sub bidders, permitting, procurement, manufacturing, factory testing, supply of all equipment (also including spare parts, consumable, special tools and handling equipment, etc.), transport to site, storage on site, erection, construction, commissioning and performance testing of the systems.

works and services related to preparation, civil, mechanical, electrical, instrumentation and control (I&C) and communication works including all required equipment for the execution of these works and services,

providing security on site during construction as per insurance requirements and the security technical specifications of the Employer as per all applicable regulations, codes and standards

providing training of personnel according to Employer´s Requirements

providing operation and maintenance (O&M) services during the initial 2 years operation

ensure occupational health, safety and environment for construction and operation of the plant

The Contractor shall be responsible for detailed design, engineering and building of the overall system, consisting of:

Battery storage system with storage batteries, bi-directional battery inverters (if applicable grid building inverters), containers to store the storage battery system, battery management and monitoring system and controller, UPS, DC cabling, AC cabling, communication cables, earthing, electricity meters and sensors, electrical connection to the existing system. The system must have compatible provision to share live data with the central SCADA.

Energy Management System capable of integrating and synchronising the existing Diesel Generators and it must be compatible with the central SCADA to exchange live data.

It is the sole responsibility of the Bidder to design, engineer and plan all related work and installations, buildings, sub-systems, elements, system facilities, equipment, services, including system hardware and software.

The Contractor shall collect and investigate all basic data which are needed for a proper design, planning and engineering. This includes, but is not limited to:

conduct site visits and basic evaluation needed for a proper design and engineering

survey of existing installation locations with regards to condition and suitability for proposed installations

review of static calculations and where such are not available static verification of the proposed locations

survey for suitability of proposed installation locations for equipment like storage batteries, inverters, controllers and other devices

survey related to the grid upgrade works which include but not limited to cable routes from BESS to grid in each island, condition assessment of low voltage distribution boxes, LV distribution boards in Powerhouse, LV distribution boards in substations, MV distribution network (where applicable) etc.

The Contractor is responsible for import, transport, storage and handling of any equipment and material needed for installation and implementation of services.

The Contractor shall provide complete engineering data, calculations, drawings, reports, manuals for Employer’s review, approval and records.

The Bidder shall include in its scope all facilities and equipment necessary for the generation of power from the system and all works and services including workshop and store equipment, special tools and handling equipment, spare parts, consumables, etc. necessary for complete, safe, reliable, and efficient operation and preventive and corrective maintenance of the system.

The scope includes also works not explicitly stated in Section 6 or elsewhere in the tender document, but which are reasonably required for the installation and operation of the systems according to good engineering practice.

All deliveries and works shall meet or exceed applicable requirements set forth by the latest edition of the following international and national codes and standards or their equivalents. In addition, all local rules and regulations shall be strictly adhered in all respects.

ISO/IEC

EN

ISA (International Society of Automation)

IEEE

ITU (International Telecommunication Union)

Maldives local regulations

No claims for extras will be considered in respect of failure by the Bidder to comply with any of the above.

Reputable manufacturers shall manufacture new equipment, which shall be subject to Employer’s review and approval. Used, reconditioned, or salvaged equipment or material shall not be allowed. All equipment used in connection with the project shall be of proven design for the intended use of the equipment. As a general principle, the latest, commercially proven, most modern and up-to-date technologies will be selected, and licensing terms agreed with the objective of maximizing value to the Employer.

All parts of the plant shall be suitable in every respect for continuous operation at maximum efficiency as well as part loads and minimum load, under consideration of the climatic conditions peculiar to the site and environmental restrictions.

The Bidder shall apply a well-established component classification and identification system. The international SI system of units shall be used for design, drawings, diagrams, instruments, etc.

Project language is English. This applies also to any kind of documents, drawings, manuals, etc.

The individual islands are described in detail in Chapter ‎2 Site Specifications. Any specification which is not provided in Chapter ‎2 but needed for a proper design, engineering, implementation, O&M services and any related work shall be investigated by the Bidder.

Disclaimer: Source of all satellite pictures shown in this Tender is Google Earth.

# Site Specifications

## General

The following section describes the specific island and its site conditions as well as climate logical parameters for the atoll.

The Bidder is responsible for its own investigations to establish sufficient and accurate information for the design of the Plant. The Contractor shall visit the proposed sites and shall ascertain the nature and location thereof and all conditions which may, affect design/layout of the BESS and Energy Management System (EMS), and the project costs.

The Bidder shall make its own assessment of any and all of the information provided in this Bid and collect own information. Neither the Employer nor any representative or advisor is responsible for the accuracy or completeness of any such information.

## Logistic

The Contractor is free to choose the seaport of entrance. There are a several seaports. Upon arrival at one of these ports the Contractor shall take care of the clearance. However, Employer shall provide the relevant supporting documents to the Contractor. After clearance it is the Contractor’s obligation to continue delivery up to the final destination at the respective islands.

## Hybrid mini-grid systems and general behaviour

For systems with Grid Building Battery Inverters (GRIDB), the main control unit shall turn off the Diesel Generators completely, if the available solar energy and the State of Charge (SOC) of the battery allows it. Solar energy shall always be the prioritized energy to be used in the system, and Diesel Generators (DG) shall only be turned on if necessary.

The system should also allow operation of multiple masters (grid forming entities such as Battery or Diesel Generators) and only use PV as a slave. If one master fails, the other master units should be able to run the grid giving the system extra redundancy.

The Battery inverter must be synchronized to other voltage sources in both cases: i) Battery inverter is online first and the other voltage source (DG, Grid, other Battery Inverter) must be synced to the battery inverter, ii) Other voltage sources are online first (DG, other Battery Inverter), the battery inverter must be synchronized to them. Especially when a static (isochronous) voltage source such like an DG without synchronization capability the synchronization must be done with an external sync check and breaker. The measurement of the requirement parameters of voltage, frequency etc. must be done fast and accurate enough to guaranty synchronization.

### Categorization of Renewable Energy Projects under ASSURE Framework

The aim of this categorization is to identify various types of renewable energy systems that incorporate photovoltaic (PV) technology and DGs with or without energy storage solutions. Three main types are defined as:

- Type A PV + DGs

- Type B PV + DGs + Small-scale BESS for grid support

- Type C PV + DGs + Large-scale BESS for shutting down DGs

### Type C Hybrid system: PV-DG-Grid forming battery

During the day, the PV and battery system provides 100% of the load and charges the battery. If battery is fully charged and PV output power is higher than the loads in the system, the PV power can be curtailed by frequency droop control and additionally commands via Fiber Optics Cable (FOC) connection.

The battery is discharged during the night until the defined minimum State of Charge is reached.

Diesel Generators are used as backup and started to provide energy to the load when the SOCmin of the BESS is reached.

The communication between the hybrid system controller (located in the powerhouse) and the PV inverters can be performed via frequency droop to curtail the active power when needed.

### Type C: Energy distribution (typical day)

The following graphics present the power production from each energy source (PV, Diesel Generators, Battery) for type B and C of hybrid systems in order to help understanding the functioning of the controller simulated and how the energy is distributed between the different power sources. Two typical days of an island were chosen and are analysed.

Figure ‎2-1: Simulation of energy distribution over 2 typical days (Type B: PV-Diesel-grid support battery)

Figure ‎2-2: Simulation of energy distribution over 2 typical days (Type C: PV-Diesel-grid forming battery)

The functioning of the hybrid systems of Type B and the relative benefit provided by the grid supporting battery can be observed by comparing the two first figures:

- for the first day in both graphics there is enough PV power to possibly cover the whole load in the system. For Type B systems it is necessary to have a generator running at all times, as the grid building function of the battery inverters is not activated. It is to be noted that in Type C the generator power (red line) drops down to zero and the generator is completely shut down, whereas for Type B the generator remains running at its minimum partial load.

- for the second day represented on the figures, the following small difference can be observed: In the case of Type B (Figure ‎2-1) the grid support battery provides additional spinning reserve to the hybrid system and as a result the controller starts the smaller Diesel Generator (125kW) and preventing excess of energy in this specific case. This situation happens when the available PV power and the load are relatively high at the same time.

- The Type C (Figure ‎2-2) with a “small” grid forming battery inverter shows that the Diesel Generators can be turned off during the day as soon as the PV power exceeds the load and the battery State of Charge is high enough. Therefore, higher diesel savings and significant running hour reductions of the Diesel Generators can be achieved.

### Other technical characteristics

Regarding the energy management system and associated infrastructure, all islands should be readily available to future upgrade/downgrade to any of the type A or B.

## Other design characteristics

### Load profile

The islands show a fluctuating energy consumption usually with morning (around 12 am) and evening (around 10 pm) peaks. Last few years recorded data show little seasonality.

A yearly demand load growth for each particular island has been estimated with data provided by the utility. The considered planning horizon is 2025.

Figure 11: Typical Daily Load Profile for 2019 and 2024

### Diesel Generators

Each island runs with minimum of three Diesel Generators. It is out of the scope of this tender to install new Diesel Generator. However, the Contractor is responsible to integrate the existing Diesel Generators within the EMS of the Hybrid energy mini grid and provide main signals to the central SCADA. Furthermore, EMS shall not be limited by number/size/model of Diesel Generators and shall be able to accommodate future changes in number of DG’s and size.

## Summary of the characteristics of the BESS to be built

The Contractor shall implement the described systems on the all the atoll as summarized in the tables below.

| Island | System Type | battery and battery inverter required minimum power | Minimum required battery capacity | Energy Management System (EMS) | Type of PV systems to be integrated to the system |
| --- | --- | --- | --- | --- | --- |
| Faafu atoll |  |  |  |  |  |
| L06 – F NILANDHOO | Flow | 500 kW | 2,000 kWh (*1) | Yes | 1,200 kWp floating solar |
|  | Non-Flow (Type C) | 500kW | 1,000 kWh (*2) |  |  |
| Sum |  | Total installed Battery inverter power: 1,000 kW | Total installed Battery Capacity: 3000 kWh | EMS: 1 |  |
| Haa Alifu Atoll |  |  |  |  |  |
| A10 – HA DHIDHOO | Flow | 500 kW | 2,000 kWh (*1) | Yes | Rooftop and ground mounted |
|  | Non-Flow (Type C) | 1,500kW | 1,000 kWh (*2) |  |  |
| Sum |  | Total installed Battery inverter power: 2,000 kW | Total installed Battery Capacity: 3,000 kWh | EMS: 1 |  |
| Sum | Type C | Total installed battery power across 2 islands: 3 MW | Total Battery capacity across 2 islands: 6 MWh | Total EMS across 2 islands: 2 |  |

(*1) During the lifecycle of flow BESS, the following capacity is required.

2,000 kWh at the initial

1,900 kWh as the norm at the end of lifecycle

1,700 kWh as the minimum at the end of lifecycle

(*2) During the lifecycle of flow BESS, the following capacity is required.

1,000 kWh at the initial

700 kWh as the norm at the end of lifecycle

600 kWh as the minimum at the end of lifecycle

Table ‎2-1 : Summary of BESS & EMS System to be installed in each atoll

## L06 F Nilandhoo island

The island is located in the Faafu Atoll.

The general data of the island is shown in the following table:

| Island code, name | L06 - Nilandhoo |
| --- | --- |
| Atoll name | Faafu |
| Utility | FENAKA |
| GPS coordinates | 03°03′20″N 72°53′28″E |
| Inhabitants (approx.) | 1,663 |
| Harbour type | Harbour 185x100x5m |
| Powerhouse Location | 3°03'33.25" N 72°53'19.95" E |

Table ‎2-2 : L06 - Island identification and general data

A map of the island provided in the next figure

Figure ‎2-3 : L06 – Map of island

### Load profile

The island has a fluctuating energy consumption. The forecasted average peak load for the target year is 947 kW with a consumption of 12,500 kWh.

### Diesel Generators

4 Diesel Generators of different sizes are installed on the island.

The following Diesel Generators are currently used.

| Item | Diesel Generator 1 | Diesel Generator 2 | Diesel Generator 3 | Diesel Generator 3 |
| --- | --- | --- | --- | --- |
| Engine manufacturer & Engine Model | Cummins KTA50-G1 | Cummins KTA38-G2 | Deutz BF8M1015C | Cummins KTA50-G3 |
| Engine power rating (continuous) [kW] | 800kW | 600kW | 400kW | 1000kW |

Table ‎2-3 : L06 Diesel Generator currently installed

### Grid Infrastructure

#### The Electrical system

Generation: 400/230V

Frequency: 50 Hz

Phase and type: three phase Wye, earthed neutral, four wire system

Distribution Network: Low Voltage (400V) / Medium Voltage (11kV)

The powerhouse in Nilandhoo Island have four Diesel Generators that supply the complete load requirements of the island.

Generators are connected to a single bus bar at low voltage (230/400V). There are existing synchronizers for generation connection and also manual load following operation strategy defined by the powerhouse operators. Distribution losses are almost entirely losses in low voltage distribution cables as there is almost no electricity theft, as the customers’ meters are generally accurate. For this island the distribution losses are estimated to be 5-15% of the total generated energy.

Electrical supply to single phase consumers is commonly 230V, single phase, earthed neutral, two wire connections and for three phase consumers it is (400/230V) Wye, earthed neutral four wires.

The Single Line Diagram for Nilandhoo is shown in Figure ‎2-4Figure ‎2-4 : Single Line Diagram for reference.

Figure ‎2-4 : Single Line Diagram for Nilandhoo Island

## A10 Dhidhoo island

Dhidhoo is one of the inhabited islands of Haa Alifu Atoll. The general data of the island is shown in the following table:

| Island code, name | A10 Dhidhoo |
| --- | --- |
| Atoll name | Haa Alifu |
| Utility | FENAKA |
| GPS coordinates | 6°53'16.60" N 73°06'49.55" E |
| Inhabitants (approx.) | 4,186 |
| Harbour type | Harbour 395x75x5m |
| Powerhouse Location | 6°53'17.33" N 73°06'47.11" E |

Table ‎2-4 : A10 - Island identification and general data

A map of the island and potential locations for PV are next provided

Figure ‎2-5 : A10 - Map of island

### Load profile

The island has a fluctuating energy consumption. The forecasted average peak load for the target year is 1981 kW with a consumption of 25500 kWh.

### Diesel Generators

3 Diesel Generators of different sizes are installed on the island.

The following Diesel Generators are currently used.

| Item | Diesel Generator 1 | Diesel Generator 2 | Diesel Generator 3 | Diesel Generator 3 |
| --- | --- | --- | --- | --- |
| Engine manufacturer & Engine Model | Cummins QST30-G4 | Cummins KTA50-G3 | Cummins QSK-38G2 | Cummins KTA38-G2 |
| Engine power rating (continuous) [kW] | 800kW | 1000kW | 800kW | 600kW |

Table ‎2-5 : A10 - Diesel Generators currently installed

### Grid Infrastructure

#### Electrical system

Generation: 400/230V

Frequency: 50 Hz

Phase and type: three phase Wye, earthed neutral, four wire system

Distribution Network: Low Voltage (LV)

The powerhouse in this Island has four Diesel Generators that supply the complete load requirements of the island. The requirement related to existing Diesel Generators and associated systems are described in the above sections.

The island is fed through the low voltage distribution network connected to the main low voltage distribution board of the powerhouse. The island is fed through LV distribution boxes located across the island and connected in a loop-in loop-out low voltage distribution network from the main low voltage distribution board of the powerhouse.

Electrical supply to single phase consumers is commonly 230V, single phase, earthed neutral, two wire connections and for three phase consumers it is (400/230V) Wye, earthed neutral four wires.

EMS is present on this island to control the DG, PV, and small BESS.

The Single Line Diagram for Dhidhoo is shown in Figure ‎2-6 for reference.

Figure ‎2-6 Single Line Diagram for Dhidhoo Island

# Technical specifications

## General

The following sections describe the general requirements for design, manufacturing, installation, testing and commissioning of all components related to BESS and EMS.

Beside all the component specific documentation to be delivered, the Bidder shall also provide at least:

For minimum technical requirements, Section 4, “Data Sheets”.

A general Layout showing the overall design of the BESS system, including positioning of containers or any other choice of battery hosting structure, positioning of inverters, architecture of EMS, controllers, transformer, and grid connection of BESS system. A two-dimensional drawing in PDF format is required.

Proposed daily operation for the hybrid systems

A general Single Line Diagram (SLD)

A Single Line Diagram (SLD) of generator control panel and distribution panel

Sizing calculations

Cable schedules

Modification design

## Battery Energy Storage System (BESS)

The BESS mainly consists of the following parts:

Flow battery

Battery Inverters for flow battery

Non-flow battery

Battery Inverters for non-flow battery

Container

The system shall operate fully automated, be remotely monitored and be delivered as a turn-key system.

The BESS is mainly designed to support the Diesel Generator system with active and reactive power following the command of the EMS. The type of battery shall be a power battery that can deliver a high power for a short period of time.

The function of the BESS is to store and supply energy as required, in accordance with the hybrid system’s energy demand.

The BESS shall perform but not be restricted to the following functionalities:

Power balancing: The BESS shall ensure an instantaneous active and reactive balance between load and generation. The system shall stabilize the frequency of the grid independently of the changes on load or renewable generation systems.

Contribution to voltage regulation: The power electronics part of the system shall contribute to the voltage regulation of the grid, performing a proper management of the reactive power circulating in the grid.

General additional requirements to the system operation:

  - The BESS shall be designed to require minimum maintenance, meaning that no specialised regular works or software updates from the BESS supplier shall be required for a continuous operation.

The Bidder will inform about the requirement of some kind of preventive maintenance scheduling and the impact of these labours on the warranty terms and conditions of the system.

The Bidder will also inform about the indicated personnel to perform the above-mentioned maintenance tasks (manufacturer, certified sub bidder, etc.)

The BESS shall have low environmental impact. A cradle to grave life-cycle assessment shall be included in the product design and all the environmental considerations will be supplied by the Bidder. The life-cycle assessment shall comply with ISO standards ISO 14040, ISO 14044 and ISO 14025.

The Bidder shall provide all the safety considerations of the battery manufacturer about the system and shall supply all the ancillary systems that may be needed to avoid.

The Bidder shall have a program for battery dismantling and return to factory after its operation life.

Battery Management System (BMS) shall be equipped with the BESS. The BMS shall monitor the status of the BESS, store operation data, and remotely control the BESS in accordance with the EMS command control.

### Flow Battery

Technical requirements of the storage battery:

The measured DC round trip efficiency: ≧ 80 %

The storage battery itself shall then be composed of cell stack, electrolyte tank, auxiliary equipment like heat exchanger, pumps, sensors, and all of these shall be installed inside containers.

The electrolyte of the storage battery shall be vanadium.

The storage battery shall be able to deliver the minimum required power as specified in Chapter ‎2.5 (column “flow battery and battery inverter required minimum power”) and meet the requirements of minimum battery capacity at nominal discharge output (column “Minimum required flow battery capacity”).

Recycling certificate: when the storage battery has achieved its end of life it must enter in a recycling program from the Manufacturer. The transport and shipment costs will be carried by the Employer. The Bidder shall provide a certificate proving that the Manufacturer agrees to receive and recycle the storage batteries according to international applicable standards.

If electrolyte of the storage battery needs to be filled into the tank on-site, the necessary tools and equipment shall be transported.

The cycle life and durability of the storage battery is a major requirement in the system. The Bidder shall provide components that full fill the following points:

  - The lifetime of flow battery applied shall be minimum 15 years, and 20 years as the norm, at DOD (depth of discharge) 100% at nominal output power.

  - Copy of the manufacturer's test report opened to public, submitted to external official agency, or published in reputable international journal shall be submitted in Technical Bid.

  - The Bidder shall submit the capacity calculation sheets with degradation ratio certificate of BESS to achieve requirements of capacities.

Standards compliance

  - IEC62932-2-1: Performance general requirements and test methods

  - IEC62932-2-2: Safety Requirements

  - UL1973: Batteries for Use in Light Electric Rail (LER) and Stationary Applications

The storage battery shall satisfy the following safety and environmental requirements:

  - Electrolyte tank shall provide a duplicated acid-resistant structure (i.e., having secondary containment), or the bike shall be provided around the electrolyte tank to prevent electrolyte leakage even when the whole amount of the electrolyte flows out of the electrolyte tank.

  - Cell stack of the storage battery shall be UL1973-certified or compliant with UL1973.

  - The storage battery shall be compliant with Annex B (Safety Requirements for Stacks) of IEC62932-2-2 (Flow Battery Energy Systems for Stationary Applications - Part 2-2: Safety Requirements). The bidder shall submit past implementation results as evidence.

  - The bidder shall submit the seismic design document of the electrolyte tank and the battery container.

Environmental condition shall be as follows:

  - Ambient operating temperature: -5 to +40 degrees Celsius

  - Operating humidity: 0 to 80 % RH

  - Enclosure rating: IP54

  - Maximum elevation: 1,000 m

Earthquake resistance shall be as follows:

  - Horizontal: 1.0 G

  - Vertical: 0.5 G

    - Battery Inverters for Flow Battery

- The battery inverters shall be bidirectional and act as inverter and charger to storage batteries.

- For each island, the battery inverters must be able to deliver the required power as stated in Chapter ‎2.5 in both directions (nominal power).

- Minimum conversion efficiency: ≥95% (one way)

- It is preferred to have the same size of battery inverters for all islands to be able to have a fast change from the spare part storehouse.

- The battery inverters shall be able to provide sufficient short circuit power to the system. The required currents must be in accordance with the grid protection concept and the grid study.

- The Bidder shall be available on site for the repair or exchange of parts within 72hours.

- The battery inverters shall be equipped with suitable DC-breakers and fuses for the battery strings, they shall both be easily accessible and exchangeable.

- The battery inverters DC voltage range needs to fit the battery voltage range, to ensure a full utilisation of the installed battery capacity.

- On the AC side, the battery inverter shall be equipped with circuit breakers and disconnectors.

- The battery inverters shall have isolation supervision.

- The battery inverters shall be connected to a dedicated feeder on the main LV distribution board of the powerhouse.

- The battery inverters shall be capable of active/reactive regulation of output power to meet the main power demand of the load in the P/Q operation mode. The maximum response time shall be less than 20 ms (twenty milliseconds) and must act faster than the Diesel generators which has a response time of 20 ms.

    - No-flow Battery

The non-flow battery shall be able to deliver the minimum required power as specified in the 2-1 in Chapter ‎2.5 (column “Battery and battery inverter required minimum power”) and meet the requirements of minimum battery capacity at nominal discharge rate (column “Minimum required battery capacity”, example given for a 1C battery).

Technical requirements of the battery:

- Suitable technology: Lithium-ion

- The non-flow battery shall be able to supply the required power as stated in the table in Chapter ‎2.5 (column “Battery and battery inverter required minimum power”).

- Acceptable nominal discharge-rate : 1 C to 2C as long as the required functionalities and specifications are fulfilled: depending on the nominal discharge rate (C-Rate) of the battery offered by the Bidder, the minimum required battery capacity specified in the 2-1 Chapter 2.5 for 1C (nominal discharge rate) batteries shall be adapted by the bidder if battery with different C-rates is provided.

- The non-flow battery itself shall then be composed of modular racks, which consist of several battery trays which are put together from modules. The modules, trays and racks shall easily be exchangeable on site to improve reliability in case of fault and to facilitate the maintenance works.

- Communication protocol with the Main Hybrid Controller: Modbus

- Battery roundtrip efficiency: ≥ 85%

- The non-flow battery shall be certified under IEC 62133-2: 2017 (or UL 62133-2) or IEC 60896-22.

- The bidder shall provide a valid test certificate issued by a ISO17025 /ISO17065 certified test laboratory.

- Recycling certificate: when the non-flow battery has achieved its end of life it must enter in a recycling program from the Manufacturer. The transport and shipment costs will be carried by the Employer. The Bidder shall provide a certificate proving that the Manufacturer agrees to receive and recycle the batteries according to international applicable standards.

- The cycle life and durability of the non-flow batteries is a major requirement in the system. The Bidder shall provide components that full fill the following points:

- The cycle DoD (Depth of Discharge) graph from the battery manufacturer shall be provided by the Bidder (official statement signed from Manufacturer required)

- The battery must be able to provide a minimum of 5,000 (Six thousand) cycles at 80% of DoD at 25°C. End of Life shall be 60% of initial capacity. The guaranteed cycle life shall be depending on the energy throughput. The Bidder shall provide a lifetime graph from the manufacturer, showing number of cycles vs. DoD.

    - Battery Inverters for non-flow Battery

- The battery inverters shall be bidirectional and act as inverter and charger to batteries.

- The battery inverters shall have capability to operate parallel in voltage source mode while DG’s are running as grid-forming element

- For each island, the battery inverters must be able to deliver the required power as stated in Chapter ‎2.5 in both directions (nominal power).

- Minimum conversion efficiency: ≥94% (one way)

- The battery inverters shall be configured for a grid building operation.

- The battery Inverters shall always be able to operate in parallel with a Diesel Generator and communicate with the Main Hybrid Controller via Modbus.

- The battery inverters shall be able to operate in power-frequency-droop control. Adjusting of droop curves shall be possible during operation without a system shutdown.

- The battery inverters shall be able to provide sufficient short circuit power to the system. The required currents must be in accordance with the grid protection concept and the grid study.

- The Bidder shall be available on site for the repair or exchange of parts within 72hours.

- The battery inverters shall be equipped with suitable DC-breakers and fuses for the battery strings, they shall both be easily accessible and exchangeable.

- The battery inverters DC voltage range needs to fit the battery voltage range, to ensure a full utilisation of the installed battery capacity.

- On the AC side, the inverter shall be equipped with circuit breakers and disconnectors.

- The battery inverters shall have isolation supervision.

- The battery inverters shall be connected to a dedicated feeder on the main LV distribution board of the powerhouse.

- The battery inverters shall be capable of active/reactive regulation of output power to meet the main power demand of the load in the P/Q operation mode. The maximum response time shall be less than 20 ms (twenty milliseconds) and must act faster than the Diesel generators which has a response time of 20 ms.

### Container

The BESS system with cooling system shall be installed inside the container. The container shall be installed next to the FENAKA powerhouse where the genset power system is located. The potential installation sites for the BESS are shown in Figure ‎3-1. If additional space for installation is required, the Contractor shall submit the drawings showing required space for prior approval of Employer and/or Employer’s representative.

Only under explicit Client authorization it would be possible to provide the system in a pre-wired ISO-Container that shall be installed next to the powerhouse. It is mandatory to use proper concrete foundations for the container. In case of powerhouse re-allocation, a pre-wired ISO-Container is mandatory. The following specifications for the BESS container have to be fulfilled:

The size of each container shall not be more than 40HC feet type and shall accommodate equipment and component mentioned at Chapter 3.2.1, and shall be salt weather resistance finishing, to adopt local weather at least 20 years.

The substructure shall be designed to withstand all dead loads and live loads including wind, ceiling, mechanical and electrical systems. For installation of container, flat concrete base of adequate size shall be designed considering the total weight of container.  Substructure must be included ground beam, pad footing and reinforcement, and excavation not exceeding 900 mm from ground level.

Painting: Two coats of emulsion paint on cement plastered walls and concrete surfaces to be applied. Exterior walls should be applied with weatherproof paint. Allow for applied 1-coats of Alkali Resisting primer on all plastered surfaces. The paint coating shall be suitable for hot and saline environments.

The air conditioning system should have sufficient cooling capacity to remove excess heat from the battery room and maintain the temperature within the recommended operating range for the BESS used. The system should be designed to ensure proper air circulation within the room, preventing the formation of hotspots.

It shall be equipped with a redundant inverter air conditioning system, where a failure of one system will not lead to a complete failure of the battery system. A failure in the air conditioning system must be communicated to the operator via a control system. This can be done with a temperature sensor inside the battery inverter room. The air conditioning system shall be built using reliable brand of air conditioners which are available locally or which could be easily replaced with similar brands in local market.

The ambient battery temperature and surrounding air humidity shall always be kept within the manufacturers’ specifications.

For a maximum cooling efficiency, the container of the BESS must have a thermal insulation on walls, ceiling and floor.

If containers are used, they shall be painted white, and coating must be according to corrosion protection class 5 for maritime environments. The container shall be salt weather resistance, waterproof, dust proof, vermin proof and body of container shall be electrically grounded and accommodate all above contains adopting local weather at least for expected life at 20 years, with proper maintenance instruction.

IP54 standard shall be used for the ISO-Containers.

A fire & smoke detection system shall be installed in all rooms/containers of the system. In case of fire, a visual and audible alarm has to be activated. The fire protection system shall be equipped with a UPS system to ensure functionality even in case of grid failures.

(a) The powerhouse in Nilandhoo Island

(b) The powerhouse in Dhidhoo Island

Figure ‎3-1 Potential installation sites for the BESS (red rectangle).

### Protections

#### AC protections

AC overvoltage protection

AC undervoltage protection

Electromagnetic Interference filter (EMI) filter

Grid voltage variations

Frequency failures

Asymmetric currents

Voltage sag compensation

#### DC protections

DC overvoltage protection

DC undervoltage protection

Inverter shutting down overload error

Inverter system isolation detector

#### Others

Output coil and IGBT over-temperature

Breaker protections of auxiliary systems

Standards

The power storage system to be implemented must comply with international standards in the applicable fields, e.g.:

| IEC 62932-1 | Flow battery energy systems for stationary applications – Part 1: Terminology and general aspects |
| --- | --- |
| IEC 62932-2-1 | Flow battery energy systems for stationary applications – Part 2-1: Performance general requirements and test methods |
| IEC 62932-2-2 | Flow battery energy systems for stationary applications – Part 2-2: Safety requirements |
| IEC 62133-2 | Secondary cells and batteries containing alkaline or other non-acid electrolytes – Safety requirements for portable sealed secondary lithium cells, and for batteries made from them, for use in portable applications |
| IEC 60896-22 | Stationary lead-acid batteries – Part 22: Valve regulated types – Requirements |
| UL 1973 | Batteries for Use in Light Electric Rail (LER) Applications and Stationary Applications |
| IEC 61427 | Secondary cells and batteries for photovoltaic energy systems |
| IEEE 1375 | Guide for the Protection of Stationary Battery Systems. |
| EN 50272-2 | Safety requirements for secondary batteries and battery installations. |
| EN 50178 / IEC 60950 | Electronic equipment for use in power installations |
| IEC 62040-2 | Uninterruptible power systems (UPS) – Part 2: Electromagnetic compatibility (EMC) requirements (IEC 62040-2:2005) |
| IEC 62093 | Balance-of-system components for photovoltaic systems – Design qualification natural environments |

## Civil and Mechanical requirements

### General

The design, execution and performance of civil and mechanical works shall follow the requirements laid down in the Maldives National Building Code 2008 and subsequently released compliance documents (e.g. Approved Document for Maldives Building Code Structure Clause B1 and Durability Clause B2), which shall be state of the art, functional and complete in all parts. Acceptable solution or verification method described in a compliance document is automatically deemed to comply with the Code.

Other alternative ways of design can be used, provided these can be demonstrated to the satisfaction of the regulating agency as meeting the required performance standards stipulated in the Building Code. These other methods are alternative solutions and need to be approved by the regulating agencies before a building consent can be issued based on the alternative solution.

### Applicable Standards

The latest editions of the British Standards as per Approved Document for Maldives Building Code Structure Clause B1 and Durability Clause B2 are valid for the construction of structures. The list does not claim to be complete but serves as a minimum framework for all works.

### Earthworks

#### General

The design and execution of the earth works shall be state of the art, functional and complete in all parts. The site investigation shall be carried out in accordance with BS 5930-2015; Code of Practice for Ground Investigations and BS 1377; Method of Test for Soil for Civil Employing Purposes.

This specification applies to all earth and rockwork required for the construction of buildings, any types of structure and burying service lines in the ground as well as to excavation works in connection with pavement, roadwork and landscaping as far as earthwork is concerned and deals with the handling and disposal of the materials to be re-used or taken to soil dumps on or off site.

The Bidder shall satisfy himself as to the on-site conditions on the site including the nature of the strata to be excavated, obstructions, etc. Note that any existing equipment or building will be decommissioned and removed from the proposed site by the Employer.

Generally, shelter, foundations, slabs and other structures shall be founded on form bearing strata by means that all excavation work for foundations shall meet the requirements of structural analysis based on the results obtained from the soil investigation and of the available information.

Excavation shall be done to the required dimensions including required working spaces and shall be finished according to the specified lines and slopes. All necessary precautions shall be taken to cause the minimum possible alteration or disturbance to the material lying under and adjacent to the excavation final lines.

Excavations below ground-water level must be approved by the Employer and kept water-free. Contractor solely shall assume the full responsibility for both shoring and strutting of excavations and for dewatering operations.

The fill materials used are to be examined and approved. Excavated materials can be used if they can be compacted to the specified / required densities in a reasonable length of time. It shall be free of highly plastic clays, of all materials subject to decay, decomposition or dissolution, and of cinders or other materials which will corrode installed materials.

Compaction below foundations is to be performed with approved equipment, properly adjusted for the type of excavation to be compacted and the fill material to be used. After placement, even distribution, and correct adjustment of the moisture content of the fill material, it is to be compacted to at least 95 % Proctor compaction density. If the specified density cannot be achieved the material shall be excavated and disposed of as unsuitable material.

If applicable the backfilled or reinstated areas shall be protected against washouts or erosion by a layer of rip rap and the Contractor is also responsible to provide adequate flood prevention measures in and around the area of all installed facilities. The used materials must be weather- and water-proof and must not suffer any ill effects through the action of seawater.

The earthworks shall also include all landscaping works as required.

#### Execution (Assembling, Installation)

All execution works shall be in accordance with the specification.

The works shall be excavated either by hand or by use of excavating plant and tools accepted by the Employer.

Excavation by hand is required mandatory close to existing installations (if any) and/or underground services.

The Bidder shall carry out all kind of earth and rockwork for the following works as defined hereafter (where applicable):

Clearing and grubbing

Excavation of top soil

Open cut excavation including shoring and dewatering as required

Backfilling

Safety precaution during earthwork

Grading

Replacement of material

Trench excavation for service lines

Embankments and erosion protection

Landscaping

#### Safety Precaution

The Bidder shall be responsible for all necessary safety measures.

Proper strutting, sheeting and bracing, including re-arrangement of the installations when necessary, stabilization and protection of slopes, methods of excavation to reduce risks of slides shall be Bidders responsibility. The additional moving of soil resulting from such damages shall not be considered as additional work.

#### Protection of Existing Utilities and Services

During construction, the Contractor shall provide all protection for existing utilities and services as required for construction operations.

In addition to the requirements specified herein, the Bidder shall comply with the following requirements.

Use all necessary precautionary and protective measures required to maintain existing utilities, services and appurtenances that shall be kept in operation. In particular, the Bidder shall take adequate measures to prevent undermining of utilities and services presently in services.

Protect existing or new utilities and services where required by the Bidders operations and/or as required by the Employer. The Bidder shall be responsible for bracing and supporting utilities and services to prevent settlement, displacement or damage.

#### Dust Control

The Contractor shall use all means necessary to control dust on the construction site.

Surfaces shall be regularly watered to prevent dust becoming a nuisance for the public and interfering with the proper execution of the works. Waste oil is not permitted for the use as dust control.

### Foundations

#### General

Foundation works shall be performed so as to ensure the bearing of all loads without detriment for and damage to the structures. The Bidder shall choose up to date methods and equipment in accordance with relevant internationally recognized standards.

#### Civil Design

The design and engineering shall be state of the art in accordance with all relevant codes and standards, functional and complete in all aspects.

#### Design Criteria for Layout, Arrangement, Drawings, Execution

#### Foundations

Foundations for structures, equipment, transformers (with oil containment) or BESS are described where the foundations rest on the natural bearing soil. Design of such foundations shall meet with the safe loading requirements and in line with the relevant international standards. Depth of foundations shall be according to design criteria of sub-structures.

Contractor shall bear all costs for any soil improvement.

#### Shop Drawings

The Bidder shall prepare and submit for the Employer for approval, shop drawings showing in detail, profiles, sections, jointing, cast-in items, reinforcing, anchorage and fastenings to be employed in this work. The Bidder shall be fully responsible for the design of any supplementary steel reinforcement required to withstand handling and erection stresses. This reinforcement shall be clearly indicated on the shop drawings.

Approval of shop drawings shall not relieve the Bidder of responsibility or liability for structural failures of fastening devices supplied by him or for damage of any kind during handling and erection.

### Specifications for concrete structures

All buildings, equipment and material used must withstand environment with high humidity, salinity and temperature over the power plant life time.

This specification refers to exposure class ‘Aggressive, with Chlorides and Sulphates’ which is applicable to any structure exposed to occasional spray or splash from seawater or discharge water and any structure in the ground or in contact with the ground up to 0.5 m above ground elevation.

Materials (cement, aggregates, water, admixtures etc.) and mix design shall be selected in order to withstand the exposure class for the lifetime of the plant.

#### Materials

Concrete constituent materials shall mean the materials which are used in the concrete mix, as specified in this chapter or as otherwise agreed in writing. The materials shall be obtained from approved sources known to produce the required quality and with no adverse effect on the durability of the concrete.

The Contractor shall obtain the approval of Employer in writing for all materials before they are brought to site. To obtain the approval of a proposed material, the Contractor shall submit a fully documented request stating:

type of material;

for which mix it is intended to be used;

to which part of the specification it refers;

name and address of source, manufacturer, and supplier;

representative samples;

reference list for similar application;

relevant test results;

The samples will be kept for reference for the duration of the project. The test results shall include the outcome of the tests specified in this chapter. Where more than one test has been performed, the results shall be presented as average, minimum and maximum values.

Employer has the right at any time to withdraw approvals and/or to reject any material if the subsequent production test values deviate from the approved pre-test values, or if in their opinion the material does not meet the objective of the works. Employer shall have access to all sources of supply and to transport and storage facilities for the purpose of inspection and sampling.

#### Design and Pretesting of Mix

The Contractor shall select constituent materials and design his concrete mix in compliance with the environmental conditions. He shall through the specified sampling and testing, including the specified documentation from trial mixing and production trials, demonstrate that he has fulfilled these requirements.

The documentation shall be submitted to the Employer for approval in adequate time before the planned start of concrete production for permanent works. No concrete shall be placed in the permanent works until the pretesting has been completed, documented, submitted, and accepted in writing by the Employer. However, for blinding layers pretesting shall be limited to documentation of materials and compressive strength.

The pre-tested and approved mix design shall not be changed without prior written approval from the Employer. However, the approved admixture dosage may be changed +-25% as required to ensure consistent concrete properties, without prior approval, but always subject to the condition that the total amount of admixture shall be within the limits recommended by the manufacturer and within limits documented by pre-testing to give an acceptable quality.

The Contractor shall keep written records for all materials used in the works, to show that they have been tested and found in conformity. This applies also to any ready-mix supply. The Contractor shall furthermore keep records of the production quality control.

#### Concreting Workmanship

##### Planning and Documentation

Before any concreting is allowed to proceed, the following shall have been fully documented by the Contractor, found compliant, and accepted by the Employer, all in accordance with relevant chapters of this specification:

concrete materials and pretesting of concrete production;

a specific method statement with a comprehensive planning documentation for each casting;

inspection of excavations, construction joints, water stops, forms, reinforcement and embedded items;

Contractor’s notice confirming that the above has been completed and that he intends to cast the concrete.

##### Placing and Compaction

Concrete shall be delivered as close to its final place of deposit as practically possible, as quickly as possible, and always within the time limits and the temperature limits specified.

All handling of the fresh concrete into its final place of deposit shall be completed as quickly as possible and always before the initial set, by methods which will prevent segregation and loss of ingredients and in a manner which will assure that the required quality of concrete is maintained. ACI 304R cl 5.1 (General Considerations) shall apply unless otherwise stated or implied in this specification.

Concrete shall not be allowed to drop into place from a height of more than 1 meter, and dropping concrete shall not be disturbed in its vertical fall by hitting reinforcement, etc, which may cause segregation. Where necessary to limit drop heights or to avoid segregation, placing shall be by means of trunks, chutes, buckets, hoppers, etc. ACI 304R cl 5.4 (Placing) shall apply unless otherwise stated or implied in this specification.

Pumping, if used, shall be controlled so that segregation does not occur in the discharged concrete, and the loss of slump shall be within pre-determined limits.

At no time shall the fresh concrete be in contact with aluminium or aluminium alloys.

All equipment which is used in handling fresh concrete shall be kept clean and free of hardened concrete. Under no circumstances shall spilled concrete or hardened concrete be allowed to enter into the permanent works.

Compaction shall be performed to ensure that the concrete becomes a dense, homogeneous mass, completely filling the form and surrounding the reinforcement, thus achieving the desired strength, appearance, and durability.

Concreting shall not take place during rain or during storms, or until rainwater and dust has been removed from the form after such events.

##### Making good of Defects

While certain casting defects may occur in spite of all precautions, the Contractor shall do his best to minimize such defects, and he shall adjust his methods if the number, size or type of defects in the opinion of the Employer gives reasonable cause for concern.

All defects after casting shall be recorded by the Contractor and brought to the attention of the Employer before any making good is carried out.

The making good shall comply with the following minimum requirements which are intended for normally occurring defects of limited and acceptable extent.

Any defect which in the opinion of the Employer is frequent or large or unusual, including any defect which is not covered by this specification shall be subject to a specific procedure to be proposed by the Contractor for the Employer’s acceptance.

Repairs will be accepted only if they can bring the structure to the quality level of a well build new structure. If this cannot be achieved and documented, the faulty work shall be replaced.

If it is found that a significant amount of voids, cavities, honeycombs, etc, is concealed behind a surface skin of laitance or mortar, then the Contractor shall expose the full extent of the defects by sweep-blasting or by a similar method to the approval of the Employer.

##### Temperature during hardening

The maximum temperature in the concrete during hardening shall not exceed 55°, unless the Contractor can document to the satisfaction of the Employer that a higher temperature will have no detrimental effects on the strength and durability (crack-width due restraint forces) of the structure. The documentation shall take into account that higher temperatures may cause larger pores and lower durability in the concrete.

The Contractor shall always minimize thermal cracking by proper planning of the work and by taking precautions to minimize temperature differences. Thermal cracks are likely to develop in massive structures (smallest dimension more than 0.5 m) and structures with restrained movement in the hardening phase (e.g. wall/slab) unless adequate measures are taken.

The particular amendment to the standard specification may state specific limits to the acceptability of cracks in certain structures; the Contractor shall take all necessary precautions to comply with such specified limits, including but not limited to precautions mentioned in the following guidelines.

The Contractor’s planning and methods for temperature monitoring and control shall be submitted as a part of the relevant method statement. It shall be revised if experience on site shows that the adopted methods do not lead to the desired results.

Any crack which occurs in spite of the planning shall be injected to the satisfaction of the Employer, or other measures shall be taken if in the opinion of the Employer they are needed to achieve an acceptable and compliant structure.

##### Protection against Evaporation

Concrete shall always be protected against evaporation during hardening. Particular care must be exercised to implement the curing at the earliest possible stage during periods of high temperature, low relative humidity, or strong winds which alone or in combination can cause extremely rapid drying-out.

Curing shall be performed for a period of not less than 14 days. The Contractor shall keep a log record with starting and completion dates plus dates of all specified curing operations.

##### Construction Joints

Construction joints are the joints between different pours. Such joints shall be pre-planned and kept to the minimum for the execution of the work, and they shall take into account structural requirements as well as requirements to appearance. Keys or other details may be specified in the particular amendments to the specification or in the drawings, and shall always take priority over the requirements specified in this section.

Joints which are not shown on the drawings but which are considered desirable for practical reasons shall be proposed by the Contractor for the Engineer’s approval.

If kickers are used at wall or column bases, it must be ensured that the concrete in the kickers are compacted and cured in accordance with this specification. Kickers at walls shall be poured in one go with the base slab.

The alignment of joints shall generally be straight, horizontal or vertical, parallel or perpendicular to adjoining parts of the structure.

Vertical joint faces shall have a formed surface; horizontal joint faces shall be level and flat.

Reinforcement shall continue across joints.

### Protection of Concrete

Protection of concrete as specified in this chapter shall mean blinding’s, membranes, coating systems, etc., which shall be applied for the purpose of protecting the finished concrete structure against exposure to action or substances which may cause deterioration of concrete and/or corrosion of reinforcement.

#### Protection on Concrete Structures in Contact with the Ground

Foundations and concrete structures in contact with the ground shall have a protection on all earth-covered faces of the underground part as follows:

All sides and any earth-covered top of such structures shall be protected by a bituminous coating system consisting of:

a penetrating bituminous primer applied in one coat;

a high build bituminous coating with a content of fibres, applied in minimum three coats;

The total dry film thickness of the coating shall be not less than 1.0 mm.

The bottom side of the structure shall be protected by a preformed membrane. Tanking may be provided by a flexible self-adhesive impervious composite sheeting of a total thickness not less than 1.5 mm consisting of a sheet not less than 0.3 mm thick of three layer cross-laminated high density poly-ethylene, and a rubber-bitumen compound.

All preparation, priming, ancillary materials, accessories, details and workmanship for the application shall be in strict accordance with the manufacturer’s recommendations.

The overlap between the membrane under the structure and the coating on vertical faces shall be detailed by the Contractor to the satisfaction of the Employer, making sure that all faces remain protected.

The bottom-protection membrane (on the blinding concrete) shall be protected by a concrete overlay and shall be laid on a concrete blinding and protected by a concrete overlay of minimum 50 mm thickness.

#### Protection on Concrete Structures above Ground

Sea-walls and similar shore-line structures directly facing the sea shall be considered as being in a splash zone even if they are standing on the shore above the high-water level. Where such structures are exposed to spray from the surf, it may be necessary to treat them as splash zone in their full height.

Splash zones and tidal zones of structures standing in the sea shall be coated from 2 m below lowest low-water level and to the top of the splash zone. The extent of the splash zone shall be defined in the design drawings but shall generally not be less than 4 m above mean sea level. Higher levels may be relevant where the structure is exposed to surf, large waves and/ or large tidal variations.

The coating shall effectively seal the concrete from ingress of chlorides and sulphates and it shall have adequate flexibility to follow temperature movements on exposed faces without cracking. The coating shall be durable and resistant to warm saline sea-water, wave action, and UV exposure; the coating should be easy to repair and re-apply and must be available in light colours.

The successful performance of the complete coating system shall be documented on basis of similar applications in marine structures under similar climatic conditions. The guaranteed minimum service life shall be at least 15 years.

The system shall at least be equal to an epoxy-polyurethane system (solvent free epoxy base coat followed by polyurethane topping). It shall always be obtained from a well reputed manufacturer with a fully documented record from similar applications, and it must have documented test results to show that it is effective in stopping chloride ingress. The work for an epoxy-polyurethane system shall as a minimum include:

sweep-blasted of the concrete surface to remove any loosely adhering matter;

making good of casting defects after the sweep blasting;

apply levelling layer of approved cementitious material;

apply primer/sealer if recommended by the manufacturer, followed by minimum three applications of high-build layers to a minimum total dry film thickness of 350 microns, or a thickness as stated in the manufacturer’s guarantee;

### Structural Steel Work

#### Material

The steel qualities for the individual construction elements are to be chosen in accordance with UBC, chapter 22, structural steel. The steel quality is to be verified by the manufacturer’s certificate.

Other types of steel may only be used after thorough tests of the technological properties and acceptance by the Employer.

#### Workmanship

##### Drawings

All necessary drawings for the manufacture and erection must be prepared in accordance to the general time schedule and approved prior to commencement of work.

The shop drawings shall clearly indicate all different items with respect to the erection work.

A separate material recognition list shall be prepared for each building.

The item numbers in these lists must be identical to those shown in the shop drawings.

##### Design and Construction

Buildings and structures must be designed for seismic loads. SBC shall be followed.

Compatibility of dimensions and setting-out data of steelwork shall be verified by the Contractor before fabrication of steelwork commences.

All joints and connections are to be made by welding or by means of screws.

The tolerances for the steel structure must be in accordance with those for the other parts of the building.

Attention must be given to the effects of temperature fluctuation on the steel structure.

The Contractor shall make all necessary expansion joints. Movement shall be made possible by providing double columns.

The Contractor shall allow for deformation due to permanent loads and the process and sequence of fabrication, erection and construction such that the completed steelwork is within the specified tolerances.

Braces (wind braces and gable walls) which resist live loads and assure stability of the building are to be used for buildings.

Connection design shall provide adequate access for welding and inspection during fabrication. The profile of the joint shall enable satisfactory non-destructive testing to be carried out.

Special attention is drawn to the deflection limitations of the steel structures.

The maximum deflection of trusses, floor beams and girders may not exceed 1/300 of the span. For trusses the deflection due to dead load may be compensated by super elevation. The maximum deflection of rafters and spars must be less than 1/400 of the span.

The design loads for buildings are to be taken from SBC and AISC standards.

A velocity of 45 m/sec is to be assumed for calculation of wind loads.

Additional to wind loads a vertical live load for roofs is to be calculated with 1 kN/m2. Live loads for flat roofs have to be chosen according to the purpose of use.

##### Erection Program

Before starting the execution of the works, the Contractor shall furnish a detailed programme according to the general time schedule. Each month the Contractor shall provide a progress report in duplicate to the Employer, indicating the progress of work.

The Contractor shall be solely responsible for the accuracy of all relevant dimensions of the structure.

##### Manufacturer’s Instruction

All work at site, i.e. handling, storage and erection shall be carried out strictly in accordance with the manufacturer’s instructions and recommendations.

### Brickwork

#### Materials

Clay bricks and blocks, calcium silicate bricks and concrete bricks and blocks shall comply with the relevant requirements of BS 3921, BS 187, BS EN 772-2, BS EN 772-3 and BS EN 771-3 respectively. The dimensions of special bricks shall comply with BS 4729.

Clay bricks and blocks, calcium silicate bricks and concrete bricks and blocks shall comply with the relevant requirements of BS 3921, BS 187, BS EN 772-2, BS EN 772-3 and BS EN 771-3 respectively. The dimensions of special bricks shall comply with BS 4729.

The Contractor shall supply the brick samples of each type to be used together with the test certificates for crushing strength through the independent laboratory to the Employer for his approval. The crushing test shall be fulfilled according BS EN 772-2. Separate samples of each type of block taken at random from loads delivered shall be deposited for approval by the Employer. The Employer will reject any load or part load which would be determined below the required strength, uncured, under or over the required size, damage or to have any other defect which may consider detrimental to the work concerned.

Bricks and blocks shall where practicable be grooved or keyed where they are to receive plastering or rendering.

#### Workmanship

Unless otherwise specified, brick and blockwork walls shall be constructed in accordance with the recommendations of BS EN 1996.

Prior to the laying of any facing brickwork, sample panels 900 mm by 600 mm of each facing brick shall be built using mortars made with different fine aggregates, white or coloured cements, or colouring agents as directed by the Employer. When the required ingredients for the mortar have been determined and approved by the Employer they shall be used for all mortar for facing brickwork and the appropriate test panel shall be retained for reference and shall represent the standard to which all facing brickwork shall conform.

Reinforcement has to be applied in accordance with static requirements, fire rating etc.

Lugs galvanized mild steel butterfly type shall be provided at all junctions between block walls and reinforced concrete columns. These lugs are to be cast into reinforced concrete columns and built into ends of exterior wall panels. They shall be spaced vertically not exceeding 450 mm.

#### Mortar for brickwork and blockwork

Cement shall be ordinary Portland cement. Lime shall be hydrated high calcium lime or hydrated semi-hydraulic lime to BS EN 459-1. Sand shall be clean natural sand free from clay or clay film over the grains or shall be crushed natural stone of approved quality.

Both sand and crushed stone shall be to BS EN 13139. Water used for mixing mortar shall be from the same source as water used for concrete.

Lime mortar shall be used for brickwork and blockwork above the ground level damp proof course unless otherwise specified or ordered by the Employer. Such mortar shall consist of cement, lime and sand in the proportions of 1:1:6 unless otherwise specified or ordered by the Employer.

Cement and lime shall be stored at the site in a perfectly dry structure and all consignments shall be used in order of delivery. Cement and lime affected by dampness shall not be used in the works.

Vertical damp proof courses shall be approved at all door and window reveals and shall comply with BS 8215.

Contractor shall also make provision for pocket chases etc. for electrical and other installations.

Mortar shall be mixed and used in accordance with clauses 2.1.2 (3) of BS EN 1996-2 including PD 6697 (recommendation for the design of masonry structures to BS EN 1996-1 and BS EN 1996-2).

Where approved by the Employer, plasticizers or proprietary masonry cements may be used as an alternative to lime in the mortar. In this case the proportions of the mix shall be based upon the manufacturer’s instructions but shall be to the Employer’s approval.

All engineering brickwork and brickwork below damp proof course level shall be built using cement mortar.

#### Joints in brickwork and blockwork

Joints shall be broken accurately and the thickness of bed joints shall be not greater than 12 mm and not less than 9 mm.

Facing brickwork shall be finished with weathered joints 3 mm deep formed before the mortar has set.

Brickwork or blockwork for internal surfaces which are not to be rendered or plastered shall be fair faced with a flush joint made as work proceeds.

Joints in brickwork or blockwork which is to be rendered or plastered shall be raked out to a depth of 5 to 10 mm.

Separation joints shall be formed by inserting approved joint filler 10 mm thick. 4 weeks after the bricks have been laid the filler shall be raked out to a depth of 20 mm and the joints shall be pointed with mortar.

### Painting

Subject of this specification are external paints on plaster and concrete as well as internal paints on plaster, concrete, gypsum and metal.

#### Materials

All materials are to be delivered to the site in original barrels. At the latest after the drying none of the paints or coats used shall cause any odour nuisance. For control purposes the individual paints are to be different in shade as far as oil-and varnish-paints are concerned.

External paint on plaster areas:

This paint is to be carried out with plastic dispersion. It is to be capable of breathing, shall be rain-tight and completely resistant against exhaust gases of any kind. The paint is to consist of a prime coat and a finish coat. According to the suction capacity of the base, thinning with water of up to 50 % is allowed.

As far as the finish coat is concerned, the thinning is limited to 10 % however.

External paint on concrete:

This paint is to be conducted with concrete scumble glaze. It is to be capable of breathing, shall be lightfast, weather resistant and hardened against exhaust gases of any kind. The surface of this paint is to be glazing. The paint consists of a prime coat with undiluted colour and a finish coat with the same colour. The drying times between the individual paints are to be strictly adhered to.

Internal paint on plaster areas:

This paint is to be conducted with plastic dispersion. It is to be capable of breathing, shall be lightfast and wash-resistant. The paint consists of a prime coat, the so-called impregnation base, thinned up to 30 % according to the suction capacity of the base. This paint is not to rest glossy (bright) on the surface.

The second paint also consists of dispersion, however, thinned up to 10 % only. The third paint is to be thinned up to 5 % only.

Internal paint on concrete:

This paint is to be carried out exactly in the same manner as external paint on concrete. Special attention shall be paid that the finish concrete surface shall be either semi glossy or mat to avoid any reflection caused by the lighting system.

Paint on metal:

The paint on metal consists of three coats, i.e. a prime coat by twofold application of protection against corrosion according to specification. Holes, cracks etc. are to be levelled with suitable sealing material. Onto the prime coat a rubbing varnish paint of impact resisting rubbing varnish is to be applied. After the drying of the rubbing varnish the finish varnish coat is to be applied with silky lustre varnish. Structural steelwork is to be painted according to specification sections above.

#### Workmanship

For the respective paints sufficiently big samples with at least three gradations of colour are to be mixed.

The base is to be cleaned of all contaminations, influencing the paint and its adhesion capacity respectively. Loose plaster and damages respectively are to be removed or to be repaired with the same material. For repairs of plaster gypsum is to be used by no means.

The repaired surface is to be in accordance with the original surface; no application points are to show. The surfaces to be painted are to be absolutely dry, formwork lube residues are to be removed from concrete surfaces and to be pre-treated respectively so as to guarantee a perfect adhesion of the paint without spotting. Dispersion paints are to be applied with a lambskin roller, at places of difficult access suitable brushes are to be used. The paints are to be applied in such a manner that the painted surface appears as uniform surface without application points, strips, brush streaks, splashes etc. Separation lines between paints of different colours as well as delimitation lines are to be sharp and clean.

Painting works outside are to be carried out at the most favourable weather-conditions prevailing for the respective kind of paint. No painting works are to take place if the temperature of the base or the surrounding air is above 50°C.

The temperature limits indicated are to be adjusted correspondingly when using special materials. The paints are to be applied in such a manner that they appear as uniform surface without application points, strips, brush streaks, splashes etc.

Separation lines in the paint as well as delimitation lines are to be sharp and clean. In addition to the visual check on the paints pine hole check and dry film thickness shall be required by using appropriate equipment to conform the continuity of the painting and also the thickness of the coating.

After the completion of the paint the ground and body colours used, the method of rust removal, as well as year and time of the paint (from ... to ...) are to be indicated at an easily visible place with varnish paint of corresponding hiding power and durability.

Because of excellent readability the text is to be written in sufficiently big letters and numbers. The examination of the paints is conducted according to the following method:

Degree of rust removal

Thickness of the prime and finish coats

Overall dry layer

Non-porous state

Observance of the working conditions

Observance of intermediate and final drying times

Wings of doors and gates are to be treated in horizontal position. All surfaces, objects, fittings etc. which are subjected to the danger of contamination or damages are to be covered or otherwise protected according to the circumstances. Paints not in compliance with the specification are to be removed; these surfaces are to be coated again with the corresponding paint.

### Water Proofing

The waterproofing of the usable areas for the roof shall be guaranteed for 10 years for material, workmanship and other liabilities which may be caused by leaks/failure of the system. The guarantee provided by the Bidder shall be supported by manufacturers guarantee for the same period.

## Energy Management System – EMS

This chapter describes the minimum overall requirements for design, delivery, installation, testing and tuning of the overall Energy Management System (EMS) which shall be obligator fulfilled by each EMS located at the individual site locations.

The EMS shall provide interactive control and monitoring for specific parts of the PV power plants, the Battery Energy Storage Systems (BESS), Diesel Generator station and auxiliaries, as defined in this specification. Furthermore, all alarms and indications shall be available on Operator workstations. The workstations shall be located close to the Diesel Generator station or in the control room of the already existing Diesel Generator station. The EMS will be fully compatible with existing D-hybrid central SCADA located in Male.

It is within the scope and responsibility of the Contractor to design the details in especially with respect to the technical features and possibilities of the EMS System family and components finally selected for realization.

Special functions and / or exceptions and add-ons dedicated to the individual PV plants are listed in a separate specification dedicated to each plant.

### General Requirements

#### General Approach

- The system shall be a state of the art, field proven system based on microprocessor technology. The architecture shall foresee distributed intelligence comparable to an automated real-time control system for data acquisition, processing, transmission, storage and archival, graphical presentation and display.

- All components shall be of approved and reliable design with the highest attainable attributes for uniformity, interoperability and interchangeability. The design shall be modular to facilitate easy maintenance, fault diagnosis and repair of the components, and to support installation and expansion in increments.

The minimum data logging interval for all relevant parameters will be defined by the Employer during detailed design. The systems should have enough data storage capacity to store data up to 2 years. The storage process has to be managed automatically.

The EMS System provided by the Contractor should be easily adjustable to operate either with or without BESS with no need of extra specialist.

#### Scope and Limits

All components for the EMS, interfaces and interconnection at the defined destinations, including all equipment for safe, undisturbed and reliable operation, cabling, connectors, patch panels, accessories, tools, software, even if not mentioned explicitly in this document are within the scope of the Contractor.

All required interfaces and switches shall be included and provided by the Contractor.

The Bidder is responsible for delivery of the operational EMS. This includes the design, documentation, certification, supply, delivery, installation, testing and commissioning of EMS, including all associated balance of plant, meeting the functional requirements of this specification.

The scope shall include the replacement of the existing EMS on each island with a new system. The new EMS must be integrated with the existing DG, PV sites and batteries.

The scope shall also include training and capacity building of local staff to operate and maintain the system as well as provide warranties for equipment and workmanship and performance guarantees and defects liability for the complete system as a whole.

The works shall include but not be limited to the following:

- Design of the EMS

- Supply and installation of EMS including:

  - Programmable logic controllers (PLCs)

  - Software packages to allow plant operators to interrogate (and troubleshoot) the system

  - Racking and cabinets

  - Power supply converters

  - Cables and communications and media converters as required

    - All local communications at the power station, including any supporting infrastructure such as power supplies, cabinets, etc. are the responsibility of the Bidder

    - Communications to remote solar PV plants will be via fibre optic cables will be provided by others. Bidder is responsible for interfacing to this communications infrastructure.

  - Configuration settings and application backup (in native file format)

- Supply and installation of any required structures, footings, cable management

- All system lightning and surge protection as required.

- All system earthing and equipotential bonding as required, including interface to existing earth grids as relevant.

- Co-ordination with the site owner for access and coordination of activities.

- Submission of documentation as per the documentation deliverables list.

- Provide training and capacity building of local staff in the operation, maintenance and safety of the system.

- Supply of all required spares as per the contract, including storage cabinet or equivalent.

- Supply of a full set of tools required for the maintenance and operation of the system.

- Ensuring compatibility with existing equipment and other plant supplied by the Bidder – especially ensuring that the existing controllers, meters and subsystems are also compatible with the procured equipment.

- Assess data available from existing plant (Diesel Generator controller), BESS and solar PV inverters and ensure that all information required for the effective operation of the EMS is available on the EMS.

- All required interfaces and switches shall be included and provided by the Bidder.

#### Bid Documentation

The bid documentation shall describe

The full system functionality,

The main system components,

Performance and parameters (data sheets),

redundancy and/or failure measure concept,

communication interfaces,

a backup and recovery concept for the EMS,

anti-virus and malware protection,

#### Spares and spare capacity

Spare capacity on hardware level:

A minimum spare capacity at hardware level of 20 % shall be considered in the design.

Spare capacity in data network and signal transmission and processing:

Signal transmission and processing have to be prepared with sufficient capacity and spare in bandwidth, bitrate, reliable termination etc. to guarantee the reliable function of the plant.

Spare capacity

- Provide expansion capability to add or reconfigure BESS, solar PV, or Diesel Generators over the EMS life (up to 20% of initial connections as spare)

- All Input/Output modules shall include minimum 20% spare capacity.

- Spare capacity in data network and signal transmission and processing:

- Signal transmission and processing have to be prepared with sufficient capacity and spare in bandwidth, bitrate, reliable termination etc. to guarantee the reliable function of the plant.

Spare parts

- key parts (that cannot be readily repaired or replaced within 5 days) of the EMS must have spares provided. Where applicable, spares must be pre-programmed with the same program and parameters as the operational equivalent.

- All supplied spare parts shall be of same material / workmanship and interchangeable with the corresponding parts of the executed work, protected against corrosion, have identification labels.

#### Spare Parts and Special Tools

All special tools required for the operation and maintenance of the system shall be provided by Bidder.

The Bidder must provide sufficient information so that the Employer can order replacement parts for the EMS as required. Supplied spare parts and tools shall be listed in detail, including, manufacturer, model, part number, stockist, present cost and typical lead time during the design review stage.

### Main functionality

#### High Diesel efficiency

Respecting the limits of grid stability and energy spinning reserve, the system shall always be running on the generator point where the highest efficiency of the diesel system can be achieved and at the same time the maximum available PV energy to be fed in the system.

Therefore, the EMS shall chose the smallest possible Diesel Generator and have it running on a high percentage of its rated power. If sufficient PV energy is available and the system is already running with the smallest generator, the EMS will allow the DGs to go down to its minimum load and even underneath this minimum load for a certain time, depending on the manufacturers specifications. In any case the EMS always has to take care that there is no reverse current in any of the three phases.

#### Maximum PV energy to be used

In order to have the highest benefit of the solar power, the EMS should not cut the PV power until a certain minimum level of power production of the DG is reached and the BESS are charged up to a predefined maximum level. The minimum and maximum limits of the BESS shall be variable and are set at the commissioning of the system.

The system shall be designed in order to allow a DG with maximum rated capacity smaller than the actual load in the system running in parallel to the BESS and the PV system, if there is enough energy from the PV system available.

#### Emergency Mode

It is mandatory that an emergency mode for the PV inverters is implemented. This mode will automatically be activated in the PV inverters, once the communication to the EMS is lost due to component failure, communication cable break or any other reason.

Once the communication is lost, the PV inverter shall automatically change into emergency mode. The PV inverter shall then work as a normal grid connected inverter that is limited in it’s output power to a certain value that is to be set during commissioning and shall be easily adjustable by the operator at a later stage if necessary.

All other parameters on the inverter shall also be easily changeable for this specific mode and may be different to the normal operation.

#### System stability

Either Diesel Generator or BESS can act as frequency and voltage regulator (multiple master concept) and be supported by PV system with reactive and active power to serve the demanded energy.

BESS shall always be able to support the system, until a new DG is started to take over the load in case of sudden PV drops and load variations. The EMS must always react quickly enough to avoid a blackout in the system due to sudden PV drops or load increases.

#### Generator switching

It shall also be avoided to have frequent start and stop scenarios of the Diesel Generator. If an additional DG is started or the DG was switched for a bigger one, there shall be a minimum time for how long this DG has to stay online, before it is switched off or changed for a smaller one. This parameter shall be easily adjustable by the operator. Additional parameters have to be respected before a DG can be switched.

#### Load ramp

If the PV system is already providing its maximum available power to the system and the load demand is still rising the Diesel Generator has to provide this energy. If there are slow load changes, the Diesel Generator will directly serve the loads and rise its power output. For sudden load changes caused by either PV drops or load increase, or both at the same time, the BESS shall support the system. The parameter of the allowed load ramp on the DG shall be adjustable by the operator.

#### System Parameters

All limits as well as minimum and maximum values of all parameters needed to configure the system shall be easy adjustable by the controller from the controlling room on site as well as from selected users online, anywhere with internet connection. The access has to be Password and Username protected. Especially parameters like: load set-points of Diesel Generators, allowed ramp rates of generator, ramp rates of BESS, timing of BESS, all setup parameters of needed current sensors and parameters that are provided from DG controllers.

The EMS shall support at least 6 DG sets, 10 PV sites and 2 battery inverters without any modification or upgrade to the system. In addition, control logic of EMS shall be configured such that at least 10 DG sets and 3 battery inverters can be added in future without changes to the control logic.

#### Grid building system concept

For systems with Grid Building Battery Inverters (GRIDB), the main control unit shall turn off the Diesel Generators completely, if the available solar energy and the SOC of the battery allows it. Solar energy shall always be the prioritized energy to be used in the system, and Diesel Generators shall only be turned on if necessary.

The system should also allow operation of multiple masters (grid forming entities such as BESS or Diesel generators) and only use PV as a slave. If one master fails, the other master units should be able to run the grid giving the system extra redundancy.

The Battery inverter must be synchronized to other voltage sources in both cases: i) Battery inverter is online first and the other voltage source (DG, Grid, other Battery Inverter) must be synched to the battery inverter, ii) Other voltage sources are first online (DG, other Battery Inverter), the battery inverter must be synchronized to them. Especially when a static (isochronous) voltage source such like an DG without synchronization capability the synchronization must be done with an external synch check and breaker. The measurement of the requirement parameters of voltage, frequency etc. must be done fast and accurate enough to guaranty synchronization.

#### Other Functionalities

Other functionalities (or equivalents) that shall be available.

Settings Operator User level:

There will be two configurable DG control mode: Manual and Auto: the DGs are controlled by the EMS depending on the actual requirements by load, the availability of solar power, as well as the SOC of the battery system.

If the system is set to AUTO mode, the following range of setting options should be available:

• DG start/stop control mode and changeover capability between MANUAL DG CONTROL MODE & AUTO DG CONTROL MODE

• Status of the start stop control

• Activation time-based Priority Swap

• Deactivation of some DGs so that they are not considered any further for AUTO start/stop operation

• Information on the actual configuration of the DGs: Nominal power, Actual priority for the DGs (considering the presently valid priority set)

Administrator User Level:

The following range of setting options should be available in Administrator user Level

• Potential Drop in Actual PV Power

• Potential Increase in Load Power

• Minimum DGs Operating Point

• Prevent daytime discharge

• State of Charge criteria for charging/discharging

• DGs target operating point for battery discharge

• Charge battery to hold DGs set for minimum operation

• Max ramp up /. Ramp down rate for DGs.

• Diesel gen set time of use

### Main Topics of EMS

The Contractor shall provide standard hardware and software configurations to the extent possible as long as it meets or exceeds the requirements of this specification. International standards shall be applied for hardware and software interfaces to allow system expansion in terms of equipment and software functions (if required).

#### System Security

The EMS or each subsystem shall be designed in accordance with ISO / IEC 27002, ISA 99 or equivalent Standard.

For security reasons all log-in and log-out events shall be logged in the event list. All user changes and modifications to the system as well as parameter and program modification shall be logged with the exact time and operator’s assignment in the event list too. It shall be possible to print this information.

For software security, at least the following has to be provided:

Up to date anti-virus program to be delivered and installed

Up to date firewall to be delivered and installed

All access ports (USB, CF-cards, etc.) shall be included in the security scenario and protected/secured against infiltration of malware

#### Over-Voltage Protection

Those parts of the system that are electrically connected to cables leaving a building shall be fitted with over-voltage protection.

#### Grounding

The EMS equipment shall be connected via a common potential equalization bar to the earthing network Station.

The Contractor shall coordinate earthing concept and requirements with the manufacturer of the EMS and accordingly provide the earthing system that shall be approved by the Employer.

#### Labelling and Marking

All terminals, plugs, internal and external connecting cables shall be labelled durable and readable with a code approved by the Employer.

For Ethernet connectivity interfaces, only shielded cables of type CAT 6 or better shall be applied in a structured cabling according to ISO 24702 and to the description within this specification.

Fibre optic cables shall be delivered and installed according to the description within this specification.

#### Cabinets

Central Unit Servers and associated accessories shall be accommodated in dedicated equipment cabinets.

For indoor application, the cabinets shall be constructed as follows:

Standard sized steel cabinets with external painting colour as per Employer/Engineers approval

Certified for minimum IP41 protection class

Power distribution box with main filter and main switch (separate 2-pole breakers for each device)

Front-patches for LAN cabling

Cable organisers, cable trays, suspensions and termination components with strain relief for all internal and external cabling

Over-voltage protection for all devices (if required)

20 % housing space for future equipment

Ventilation fan to ensure that maximum allowable operating temperature of all equipment inside the cabinets shall not be exceeded

Bottom cable access

Document pocket

Grounding bus bar for earthing connection

Doors with glass or another material front and locking system

Inner light and power socket for maintenance

Provision of easy access for maintenance and repair, all devices with rear plugs shall be drawable

#### Electrical Interface Units

EIUs as data acquisition modules shall be designed and provided to perform the interface between the electrical equipment and the EMS. The EIU hardware shall be fitted with process interface slot-in modules for digital inputs and outputs, analogue inputs, Ethernet communication modules, etc. Output from all generating sources shall be measured directly and not through any intermediary meters such as Battery Control Units or Generator controllers.

The EIU shall be of same make and type all over the Plant and shall have Ethernet connection with EMS. The power supply of the EIU shall be powered from the UPS.

#### Performance and Reliability

All equipment shall be of high quality and reliability. The overall system availability of the EMS shall be 99% or better.

All equipment shall be protected against cyber-attacks.

#### Software Requirements

The EMS shall be based on standard proven firmware and software, which shall already been implemented in other systems. The software engineering tool shall be provided to configure, set up and modify the data acquisition, data processing and database system components. The software application shall include facilities to perform programmable logic functions.

The software tool of EMS shall provide a high degree of configurability, including but not limited to, changes in number of DG’s, BESS, PV sites, operational parameters, capacities of generating sources, remote configuration of BESS and inverters where possible.

The system shall have monitoring and self-diagnostics features for both, hardware and software.

Licensed software copy required for the proposed system shall be provided. The latest proven anti-virus software shall be installed in the EMS.

All logins to the system shall be password protected. Data transmission via public internet shall be encrypted.

### Alarm and Event Management

#### General

All alarms including system alarms and important events shall be listed up on the display. The lists shall be in chronological sequence showing:

The precise date and time with the specified resolution in actual sequential of events;

Plant identification code;

Clear text/denomination of alarms and events;

Status message (open, close, off, high, low);

The actual value in case of high/low alarms derived from analogue values;

Sorting of alarms per sub group shall be possible.

Alarms and signals that happened in the past can be recalled by the operator at any time. If any new alarm appears while monitoring any other page, flashing signal on the screen shall show the new event/signal to the operator.

Dedicated soft pushbuttons shall serve the operator for alarm handling such as buzzer signal acknowledgement, alarm acknowledgement, alarm clearing and page flipping. Differentiation between alarms and events shall be done by colour coding (e.g., Alarms: red colour). Further colour for distinction of alarms according to the degree of urgency or type of alarms is also required.

Flashing functions of alarm messages shall be according to standards related to conventional alarm.

The flashing frequency for coming and going alarms shall be different.

First out alarms shall be marked clearly and needs special acknowledgement.

#### Report Generation

Automatic and configurable generation of typical reports (total or detailed power generation data, problems, efficiency analysis, weather reporting etc.) shall be supported internally or with the help of formatted data output and provisioning of corresponding templates and input filters for e.g., MS Excel or similar. It shall be possible to print the generated reports. The format of the logs and reports shall be subject to the approval of the Employer. Reports shall be generated locally in each island as well as in Central SCADA.

### Data Communication Network

The EMS shall have the communication via Modbus TCP to all energy producers, respectively Diesel Generators, PV inverters and BESS units. It will receive all necessary measurement data from those sources, such as voltage, ampere, cos phi, battery SOC, frequency and warnings/alarms at the connection points of the sources. According to the actual state of the system it will then decide and send the control to the relevant sources, if and how they should react, be switched on or off or regulate their power output. The communication shall be realized with network cables CAT 6 and fibre optic cables for longer distances. The system shall communicate with and provide data to the SCADA system. In accordance with Section ‎3.4.7, the data for PV Plant, DG, and Battery are transmitted to the Central SCADA.

The EMS shall also be able to Include any other sensors necessary for the functioning of the system and provide the data of additionally included sensors in the Modbus protocol. The communication protocol of the sensors to be included may be of a different kind than Modbus.

The supplied system shall include a data communication network to ensure the proper interconnection of all components of the EMS such as but not limited to cables, accessories, media converters, repeaters, amplifiers, switching and routing equipment including accessories, their housing as required, as well as the management systems necessary to operate the data communication network.

Ethernet with a minimum data rate of 100 Mbit/s shall be provided.

The network shall be fault tolerant for single failure and shall at least be installed in ring structure.

Switches used in the network and to interface equipment shall be manageable and able to interface to FOC on upper-level cabling structure.

All FOC cables shall be terminated to patch panels; no fibres to be loose.

Interface to switches shall be performed via patch cables.

Underground splices shall not be foreseen.

### Power Supply & Cabling

#### General

Power supply for EMS shall be provided from UPS. All redundant devices shall have redundant power supply modules.

The Contractor shall perform all cabling and installations works for outdoor and indoor equipment as well as the interface interconnection and termination at existing devices. No cable joints shall be used for interfacing of EMS with any other equipment.

#### Additional communication cable

There shall be an additional fibre optic cable installed between the powerhouse and the council of each island. In the powerhouse the cable shall be routed to the control room where the EMS will be installed. It shall be connected to the FOC network of the power plant. In the council the cable shall be routed into a room that is selected from the council. On each side a spare cable of 20 meters shall be left.

#### Electrical connections and UPS

Redundant power supply for EMS shall be provided from UPS. A minimum of 30 min. of independent power supply shall be guaranteed for on-site conditions.

Over-Voltage Protection: Those parts of the system that are electrically connected to cables leaving a building shall be fitted with over-voltage protection. For special specifications see Chapter 3.9 Lightning protection.

Grounding: The EMS equipment shall be connected via a common potential equalization bar to the earthing network of the diesel power station building.

The Bidder shall coordinate earthing concept and requirements with the manufacturer of the EMS and accordingly provide the earthing system that shall be approved by the Employer.

Labelling and Marking: All terminals, plugs, internal and external connecting cables shall be labelled durable and readable with a code approved by the Employer. Code list shall be included in documentation.

#### Category 6 cables

At least shielded Cat 6 cables shall be used for Ethernet communication system with a length less than 100m. The cables shall be according to ISO 24702 suitable to function properly and faultless under the prevailing environmental conditions and rodent-protected for direct buried application. The cables shall have a frequency spectrum up to 250 MHz and be terminated in 8P8C modular connectors.

The cables shall be halogen free.

#### Fibre Optic Cables (FOC)

Depending on the requirements by the proposed control system single mode and / or multi-mode FOCs shall be used.

The manufacturing, construction, labelling and testing of the fibre optic cable system shall meet the requirements established in the relevant applicable ITU and IEC codes, standards and recommendations.

Application

The fibre optic cable shall be suitable to function properly and faultlessly under the prevailing environmental conditions and rodent-protected for direct buried application.

The fibre optic cable shall be laid in buried cable conduits. Therefore, a fully dielectric fibre optic cable suitable for ducted or direct buried applications, filled with compound to prevent axial and longitudinal ingress of water and / or soluble chemicals throughout the cable shall be provided. The cable shall have loose tubes as secondary coating of fibres.

Main Cable Structure

The cable shall be:

Halogen free

Metal free

Axial and longitudinal tightness against water and / or soluble chemicals

Rodent-protected

Traction elements of Kevlar

Lifetime of cable >30 years

FOC fibre with primary coating Ø 250 +/- 15µm

Secondary coating of fibres

Filled centre fibre with 24 fibres

Standard colouring

Outer cladding:

Halogen free

UV persistent

Markings containing

Manufacturer numbering

Type of cable

Number of fibres and type of fibre

Date; Metering and P/N marking

Cable markings shall be printed on the outer fibre cable jacket. The markings shall be permanent, insoluble in water and be legible for the duration of cable life. The markings shall be printed at intervals of not more than 2 meters.

Fibres and number of fibres

Diameter fibre:9 µm (+/- 10 %) – Single Mode

Diameter fibre:62,5 µm (+/- 10 %) – Multi Mode

Diameter cladding:125 µm (+/- 3µm)

Diameter coating:250 µm (+/- 15µm)

Damping: Single Mode max:

< 0,4dB/km, typ. 0,36dB/km at 1310 nm wavelength and

< 0,3 dB/km, typ. 0,26 dB/km at 1550 nm wavelength.

Multi Mode max:

< 0,9 dB/km, typ. 0,9 dB/km at 1310 nm wavelength.

Number of fibers: The long-distance cable shall contain a minimum number f 12 fibres.

#### Measurement after Cable Installation

Measurement of splices

To verify the maximum damping of splices ODTR measurement in both directions shall be performed. The max damping of 0.1 dB per splice shall not exceed.

Measurement of Cable Run from Termination to Termination

The characteristics of the cable run shall be measured and verified and protocolled by:

Bi-directional Power Loss Measurement at 1310 +30/-15 nm and 1550 +30/-70 nm

Bi-directional OTDR Measurement at 1310 +30/-15 nm und 1550 +30/-70 nm

The values for maximum damping are:

max. damping splice: 		0,10 dB

max. damping connectors (pair):	0,50 dB

#### Fibre Optic Cable Accessories

A detectable reinforced underground marking and warning tape shall be laid in the ground 300 mm above the protection conduit.

The patch cord consists of a single / multi-phase fibre optic cable with plug connections on both ends. Pigtails are fibre cables pre-assembled with a connector at one end. The fibres of the patch cords and pigtails shall be according to the specified fibres and all components shall have a service life of more than 20 years with a minimum of contact durability of 1000.

Type of connectors shall match the requirements of EMS I/O modules and shall be of same type all over the plant. Contractor shall decide the used type (ST; SC; FC/PC)

The connecter loss shall not exceed 0.5 dB per connector pair.

OTDR (Optical Time Domain Reflectometer) test report shall be submitted to Employer/Engineer.

The termination of each fibre in transmit and receive direction shall be provided on an optical distribution frame (ODF) for access to the transmission equipment. The ODF for receive and transmit direction shall be configured in accordance to the specified number of fibres (24). The ODF are to be installed in termination cabinets, which may be combined with the communication system.

#### Industrial Ethernet Switches (Managed type)

Industrial Ethernet Switches foreseen for installation shall provide the following:

Compliance:	IEEE 802.3 ISO/IEC 8802/3

Technology: 	Store and forward

Filtering Services / prioritization: 	IEEE 802.1 D/p

Port type: 	Min 100 Mbps	Media as necessary

Diagnostics: 	Indication of power status, link status, data, full duplex, 	link failure (fibre disconnected)

Management: 	SNMP, HTTP

Design: 	Fan less

Mechanical design: 	Stability against shock and vibration

Min. operating temp. range: 	0°C - 55°C

Rel. humidity: 	0% - 100%

Diagnostics: 	LEDs for indication of power status, link status, data, 	full duplex, link failure (fibre disconnected)

EMC: 	EN 55022, EN 50082-2

VLAN support:	IEEE 802.1Q, MAC Address / Port Based

MTBF:	>20 years

### List of Signals to be sent to central SCADA

The following data shall be sent from the EMS to the central SCADA in Male.

#### PV Plant

Table ‎3-1: PV Plant data to be sent to the central SCADA

| Measurement | Sub Measurement | Unit |
| --- | --- | --- |
| Active Power | Power Plant Active Power | kW |
|  | Phase A Active Power | kW |
|  | Phase B Active Power | kW |
|  | Phase C Active Power | kW |
| Reactive Power | Power Plant Reactive Power | kVAr |
|  | Phase A Reactive Power | kVAr |
|  | Phase B Reactive Power | kVAr |
|  | Phase C Reactive Power | kVAr |
| Current Injection | Phase A Current | A |
|  | Phase B Current | A |
|  | Phase C Current | A |
| Voltage | Phase A Voltage | V |
|  | Phase B Voltage | V |
|  | Phase C Voltage | V |
| Daily Active Energy | Power Plant Active Energy | kWh |
|  | Phase A Active Energy | kWh |
|  | Phase B Active Energy | kWh |
|  | Phase C Active Energy | kWh |
| Daily Reactive Energy | Power Plant Reactive Energy | kVAhr |
|  | Phase A Reactive Energy | kVAhr |
|  | Phase B Reactive Energy | kVAhr |
|  | Phase C Reactive Energy | kVAhr |
| Total Active Energy | Power Plant Active Energy | kWh |
|  | Phase A Active Energy | kWh |
|  | Phase B Active Energy | kWh |
|  | Phase C Active Energy | kWh |
| Total Reactive Energy | Power Plant Reactive Energy | kVAhr |
|  | Phase A Reactive Energy | kVAhr |
|  | Phase B Reactive Energy | kVAhr |
|  | Phase C Reactive Energy | kVAhr |
| Power Factor | Power Plant Cos Phi | - |
|  | Phase A Cos Phi | - |
|  | Phase B Cos Phi | - |
|  | Phase C Cos Phi | - |
| Plant Usage | Hours of PV Plant Usage | hours |
| Temperature | Weather PV plant temperature | ºC |
| Irradiance | PV plat Irradiance | W/m2 |
| Operating Status | Normal / Disturbance | - |
| Connection Status | Connected / Disconnected | - |
| Control Set | Connect / Disconnect | - |

#### Diesel Generator

Table ‎3-2: DG data to be sent to the central SCADA

| Measurement | Sub Measurement | Unit |
| --- | --- | --- |
| Active Power | Power Plant Active Power | kW |
|  | Phase A Active Power | kW |
|  | Phase B Active Power | kW |
|  | Phase C Active Power | kW |
| Reactive Power | Power Plant Reactive Power | kVAr |
|  | Phase A Reactive Power | kVAr |
|  | Phase B Reactive Power | kVAr |
|  | Phase C Reactive Power | kVAr |
| Current Injection | Phase A Current | A |
|  | Phase B Current | A |
|  | Phase C Current | A |
| Voltage | Phase A Voltage | V |
|  | Phase B Voltage | V |
|  | Phase C Voltage | V |
| Daily Active Energy | Power Plant Active Energy | kWh |
|  | Phase A Active Energy | kWh |
|  | Phase B Active Energy | kWh |
|  | Phase C Active Energy | kWh |
| Daily Reactive Energy | Power Plant Reactive Energy | kVAhr |
|  | Phase A Reactive Energy | kVAhr |
|  | Phase B Reactive Energy | kVAhr |
|  | Phase C Reactive Energy | kVAhr |
| Total Active Energy | Power Plant Active Energy | kWh |
|  | Phase A Active Energy | kWh |
|  | Phase B Active Energy | kWh |
|  | Phase C Active Energy | kWh |
| Total Reactive Energy | Power Plant Reactive Energy | kVAhr |
|  | Phase A Reactive Energy | kVAhr |
|  | Phase B Reactive Energy | kVAhr |
|  | Phase C Reactive Energy | kVAhr |
| Power Factor | Power Plant Cos Phi | - |
|  | Phase A Cos Phi | - |
|  | Phase B Cos Phi | - |
|  | Phase C Cos Phi | - |
| Speed | Primary Genset Speed | rpm |
| Power | Primary Genset Power | kW |
| Torque | Primary Genset Torque | Nm |
| Instant Fuel Consumption | Primary Genset Fuel consumption | l/h |
| Total Fuel Consumption | Primary Genset Total Fuel usage | l |
| Generator Usage | Hours of Genset Usage | hours |
| Operating Status | Normal / Disturbance | - |
| Connection Status | Connected / Disconnected | - |
| Control Set | Connect / Disconnect | - |

#### BESS

Table ‎3-3: BESS data to be sent to the central SCADA

| Measurement | Sub Measurement | Unit |
| --- | --- | --- |
| Active Power | Battery AC Power | kW |
|  | Battery AC Power | kW |
|  | Phase B Active Power | kW |
|  | Phase C Active Power | kW |
| Reactive Power | Power Plant Reactive Power | kVAr |
|  | Phase A Reactive Power | kVAr |
|  | Phase B Reactive Power | kVAr |
|  | Phase C Reactive Power | kVAr |
| Current Injection | Phase A Current | A |
|  | Phase B Current | A |
|  | Phase C Current | A |
| Voltage | Phase A Voltage | V |
|  | Phase B Voltage | V |
|  | Phase C Voltage | V |
| DC Site | DC Discharging Power | kW |
|  | DC Charging Power | kW |
|  | DC Discharging Current | A |
|  | DC Charging Current | A |
|  | DC Voltage | V |
| Operating Status | Normal / Disturbance | - |
| Connection Status | Connected / Disconnected | - |
| Control Set | Connect / Disconnect | - |

## Utility compatibility

### General

The applicable standard related to interconnecting an inverter to a utility network is IEC 61727: 2004, “Photovoltaic (PV) systems – Characteristics of the utility interface”. The inverter’s AC voltage, current and frequency shall be compatible with the utility system in accordance with IEC 61727.

### Normal voltage operating range

Inverter shall operate at and shall support the network voltage. The inverter shall synchronise with the utility network before a connection is established. The inverter shall not generate the voltage of the grid but shall inject current into the system.

### Flicker

The operation of the inverter, in conjunction with other existing and future loads at the same point of connection, shall not cause flicker levels to increase beyond the levels specified in IEC 61000-3.

### DC injection

The static power converter of the inverter shall not inject DC current exceeding 1 % of the rated AC output current into the utility AC. Interface under any operating condition in accordance with EN 50178 or its equivalent. This relates specifically to inverters where the static power converter has no simple separation from the utility network.

### Electromagnetic Compatibility

EMC to possible electromagnetic emissions from facilities or equipment to be installed, so the installation team is right to safe conditions of use, as well as the equipment to be connected to it. The inverter must be prepared and be electromagnetic compatible in function of electromagnetic immunity (IEC61000-6-2) and Emission (IEC61000-6-4).

### Harmonics and waveform distortion

In accordance with IEC 61000-3 and IEEE519, only devices that inject low levels of current and voltage harmonics will be accepted; the higher harmonic levels increase the potential for adverse effects on connected equipment.

Acceptable levels of harmonics, voltage and current depend upon distribution system characteristics, type of service, connected loads or apparatus, and established utility practice. The embedded generator output shall have low current-distortion levels to ensure that no adverse effects are caused to other equipment connected to the utility system.

Total harmonic distortion (THD) and odd harmonics distortion shall be less than 5% and 3% respectively at rated generator output in accordance with IEEE519.

### Power factor

The inverter shall not inject reactive power into the utility network, while the drain of reactive power shall be limited to a power factor of 85%. The inverter shall operate at these power factors in the range 10% to 100% of nominal power.

### Synchronization

The inverter shall synchronize with the utility network before the parallel connection is made. Automatic synchronization equipment shall be the only method of synchronization. The limits for the synchronizing parameters for each phase are:

frequency difference: 0,3 Hz,

Voltage difference: 5 % = 11,5 V per phase, and phase angle difference: 20°.

### Safety and protection

General: The safe operation of the inverter in conjunction with the utility network shall be ensured at all times.

Safety disconnection from utility network: The inverter shall automatically and safely disconnect from the grid in the event of an abnormal condition. Abnormal conditions include

network voltage or frequency out-of-bounds conditions,

loss-of-grid conditions and prevention of islanding

DC current injection threshold exceeded

PV field earth leakage

Inverter over temperature

Disconnection switching unit: The inverter shall be equipped with a disconnection switching unit which separates the inverter from the grid due to the above abnormal conditions.

The disconnection switching unit shall be able to operate under all operating conditions of the utility network.

A failure within the disconnection switching unit shall lead to disconnection and indication of the failure condition.

A single failure within the disconnection switching unit shall not lead to failure to disconnect.

Failures with one common cause shall be taken into account and addressed through adequate redundancy.

The disconnection switching unit shall disconnect from the network by means of two series switches. Each switch shall be separately rated to the inverter’s nominal power output. At least one of the switches shall be an electromechanical switch while the second switch may be part of the existing solid state switching circuits of a utility-interconnected static power converter. The electromechanical switch shall disconnect the inverter on the neutral and the live wire(s).

The fault current breaking capacity of the disconnecting switch shall be appropriately sized for the application.

Abnormal conditions can arise on the utility system and requires a response from the connected inverter. This response is to ensure the safety of utility maintenance personnel and the general public, and also to avoid damage to connected equipment. The abnormal utility conditions of concern are voltage and frequency excursions above or below the values stated in this clause. The inverter shall disconnect if these conditions occur. The parameters for disconnection shall correspond to those below but shall be adjustable.

Over-voltage and under-voltage: The inverter shall cease to energize the utility distribution system should the network voltage deviate outside the conditions specified in table below. This applies to any phase of a multiphase system. The system shall sense abnormal voltage and respond. The following conditions shall be met, with voltages in r.m.s. and measured at the POC (Point of Connection). All discussions regarding system voltage refer to the nominal voltage. The parameters for disconnection shall correspond to those below, but shall be adjustable in the field.

| Response to abnormal voltages |  |
| --- | --- |
| 1 | 2 |
| Voltage range (at point of utility connection) | Maximum trip time S |
| V < 50 % | 0,2 s |
| 50 % ≤ V < 85 % | 2 s |
| 85 % ≤ V ≤ 110 % | Continuous operation |
| 110 % < V < 120 % | 2 s |
| 120 % ≤ V | 0,16 s |

Over-frequency and under-frequency: The inverter system shall cease to energize the utility network when the utility frequency deviates outside the specified conditions. When the utility frequency is outside the range of 49,5 Hz and 50,5 Hz, the system shall cease to energize the utility.

Prevention of islanding: An islanding condition shall cause the inverter to cease to energize the utility network within 2 s, irrespective of connected loads or inverters. One active islanding detection method and one passive island detection method shall be used to avoid an unintentional island.

| Active and passive types of anti-islanding protection of inverters |  |
| --- | --- |
| Active type | Passive type |
| Frequency shift | Power phase jump detection |
| Active power fluctuation | 3rd harmonic voltage rise |
| Reactive power fluctuation | Frequency change rate detection |
| Load fluctuation |  |

DC current injection: The static power converter of the inverter shall not inject DC current greater than 1 % of the rated AC output current into the utility interface under any operating condition. The inverter shall cease to energize the utility network within 500 ms if this threshold is exceeded.

Response to utility recovery: After a voltage or frequency out-of-range condition that has caused the inverter to cease energizing the utility network, the inverter shall not re-energize the utility network for 60 s after the utility service voltage and frequency have recovered to within the specified ranges.

## Earthing

### General requirements

The bonding of equipment should prevent dangerous voltage differentials arising between metallic equipment during fault conditions and provide alternative conduction paths to power cables should ground surges from nearby lightning strikes arise.

The main earth point for the system shall be a systems earth electrode, as specified in Section Earth electrode. It shall be located directly below each array structure.

The earth electrode shall be the common point for the casings of all balance of system components, and the array structure.

The risk of lightning strikes varies according to location. However, for all site locations the following basic guidelines will apply, as the electrical distribution is contained within one building.

For some sites additional lightning protection circuits may be required.

### Earth electrode

Two types of earth electrode are suitable:

Spike earths

Multiple spike earths (trench earth)

Bare copper or bare galvanised steel, in stranded, strip or rod form are satisfactory earth materials in non-aggressive soils. Because galvanised ferrous materials corrode sacrificially to copper, galvanised iron and steel electrodes should not be buried in close proximity to bare copper. In aggressive soils only galvanised steel earth rods should be used. The down conductors shall be connected to copper or galvanised/stainless earth spikes of minimum length 1200mm.

The spikes shall be driven vertically into the ground till buried to a depth of at least 0.3 m. If necessary, several spikes shall be interconnected as a trench earth to achieve the required resistance.

10mm2 shall be used as earth straps to bind components to the earth electrode, no loops shall be created to avoid inductive voltage. Polyethylene (PE) cable will be wired jointly with the positive and negative unipolar cable. Under no circumstances shall connection points, bolts, screws, etc. used for bonding or earthing be utilised for any other purpose. It will be responsibility of the Bidder to supply and fit earth terminals or clamps on equipment that must be earthed where these are not provided.

.

### Equipment Earthing and Bonding

All metal equipment and casings shall be bonded together, as they are inter-connected by the power cables. The bonding shall be made using copper conductors of 10mm2 minimum. A separate conductor shall be used specifically for that purpose.

The resistance requirement in between enclosures shall be less than 1 ohm. The resistance measured against ground shall be less than 1 ohm.

The design shall base on international standards and codes like IEC or specific Maldivian standards and codes. The specific standards applicable for earthing requirements are:

IEC 60364-7-712 Electrical installations of buildings Part 7-712 Requirements for special installation locations-Solar photovoltaic (PV) power supply systems

IEC 60364-5-54 Electrical installations of buildings Part 5-54 Selection and erection of electrical equipment–- Earthing arrangements, protective conductors, and protective bonding conductors

## Over voltage protection

Lightning protection shall be designed inherently into the system configurations, earthing, and some level of surge protection shall be built into the inverters themselves.

For mitigation of overcurrent the Bidder shall follow the installation practice below:

All DC cables should be installed to provide as short runs as possible and positive and negative cables of the same string or main DC supply should be bundled together, avoiding the creation of loops in the system. This requirement for short runs and bundling includes any associated earth/bonding conductors.

Long cables (e.g., PV main DC cables over about 50 m) should be installed in earthed metal conduit or trunking or be screened cables such as mineral insulated or armoured.

Additionally, the following overvoltage protection devices shall be provided:

DC system: surge arrestors, class 2, on the inverter DC inputs or DC distribution box shall be provided.

AC system: surge arrestors, class 2, at the incoming point of supply shall be provided.  The surge arrestors shall be installed in the Main DB.

The surge arrestors shall be of class 2 with visual fault indication, 40kA (8/20) according to IEC 61643-1 for sensitive electronics, clamping voltage to less than 1,500V. Units with replaceable LP modules are required.

## Labelling, safety signs and notices

All labelling and signage must be in English. All notices, labels or signs shall be durable and not removable except by determined and deliberate action. The inscriptions shall be legible and indelible. All custom signage to be ABS plastic silk-screened quality, indelible and shall be easily noticeable.

Where possible, standard approved symbolic safety signage is to be used. All DB labels shall be professional quality signage.

In addition to the standard electrical labels required in terms of British DTI standards regarding electrical installations, the following signs are required:

| Locations | Sign number | Example design |
| --- | --- | --- |
| Main DB Main display | 1 |  |
| FENAKA Transformer Tx breaker cubicle Main DB Inverter DB | 2 |  |
| Inverter Inverter DB | 3 |  |
| Main DB | 4 |  |
| Tx Breaker cubicle | 5 |  |
| Inverter DB Long DC cable runs from array JB to inverter | 7 |  |
| Roof top locations | 8 |  |

## Noise and Radio Interference

The systems offered shall be designed, supplied and installed to minimise audible noise. The maximum allowable residual sound level is 50 dB LAeq for all electronic equipment. This requirement does not apply to the Diesel Generators.

The systems shall be screened from emitting electromagnetic interference.

No equipment may generate any radio interference with other equipment or systems and all equipment shall be suppressed to prevent interference of commercial radio and TV reception. The equipment and methods used in determining the acceptable levels of radio interference shall be as specified in IEC CISPR 22.6

## Commissioning and Onsite Acceptance Tests

Prior to delivery of the project, the Bidder must perform a series of onsite tests to verify the proper performance of every system.

The onsite test will be divided per individual systems: BESS and EMS. After performing the tests per each system, it will be performed the tests for the entire system.

Commissioning tests effectively place responsibility for system or component performance on the supplier. The commissioning tests are the responsibility of the supplier.

All the tests shall be properly documented and checked by the Project Management Team prior to the delivery of the project.

Tests shall be made on the respective electrical components, isolators and circuit breakers, metering, earthing, bonding, and operation of the data-logging system and monitoring.

### Commissioning and testing of BESS and EMS

Tests of separate control system allow at least check the correct operation of the control hardware and communications interfaces.

The Bidder will provide a detailed test plan for this system separately, which shall include at least the following items:

Visual inspection, labelling and technical specifications checking

Power supply test.

Test of communication with SCADA.

Test of command sending and reception to Diesel Generators.

Test of reception of monitoring parameters of the distributed systems

Test of communication latency

Several full charge and discharge cycles at rated and peak power will be carried out, or at least to the minimum state of charge expected to operate the system on a daily basis.

During charge and discharge testing process the  BESS shall achieve the peak power ratings at least once per complete cycle. The duration of the peak power shall be the necessary to archive the optimum control of the hybrid plant and will be within the values provided by the manufacturer.

With reference to Figure 1 of Section 1.3 in Section 3, it shall be verified that RTE (round- trip efficiency) of the  BESS at rated power align with the specifications of the  BESS submitted during the bidding process.

Communications between the battery inverter or the BMS and EMS will be tested. The tests will be performed at zero, nominal and peak power ratings of the system, in order to ensure that possible electromagnetic noise will not affect the communications.

The  BESS must communicate with EMS, so it is considered essential to carry out communications tests of these subsystems separately. Communications tests shall include both the sending of control operating commands from EMS to  BESS and monitoring parameters from the  BESS to the EMS. Tests must be conducted both at zero power and at nominal power.

The correct functioning of ancillary systems of the  BESS will be tested, including at least:

Air conditioning system temperature regulation is working correctly.

Lights

Electric Outlet

The functional performance onsite tests of the control algorithm will be carried out during the hybrid plant tests.

Tests performed onsite will let the provider to verify the correct operation of the  BESS at the final location. The test record shall include at least measurements of battery temperatures, power electronics temperatures, current and power values achieved, possible detected alarms and any other outstanding incidence that may occur. The tests of the  BESS will include at least the following features.

Mechanical completion: The mechanical completion checking will consist of the following:

Batteries power output is properly connected to the battery inverters.

Communications wiring between Batteries and Battery Inverter and Energy Management System is correctly connected.

No mechanical damages exist.

### Hybrid Plant Test

The hybrid plant tests are intended to validate the performance of the entire plant and will involve all the systems operating in a coordinated way to achieve the target of a reliable power supply of the islands, with a significant reduction on the diesel consumption.

The test of the full hybrid plant will be the last to be completed, and will require a good coordination between all suppliers, which shall be available to be present during the tests of the systems together.

The Bidder will provide the details of the test plan for the whole system, which shall include at least the following items:

Power balance tests. Through these tests the capability of maintaining the power balance in the grid versus sudden reduction in photovoltaic generation and/or increments in the loads will be verified. The tests shall include the manual reduction of the PV generation at different rates at least 25%, 50%, 75% and 90% of PV when a constant PV power of min. 80% of installed kWp is available for the AC PV connected capacity. This shall be repeated with different ramp rates (reduction of kW/sec), that have to be confirmed by the Employer.

Tests to verify the response to voltage variations will be also performed. It shall be checked that the compensation response of the system to voltage variations to be less than 1 minute.

Settings and adjustments of diesel protections and their performance versus sudden power unbalances in the grid.

Power quality tests. Measurements of all the parameter related with the power quality shall be taken during the tests phase: THD (voltage and current), flicker, frequency and voltages. All these measurements shall show the compliance with the national requirements, as well as the technical requirements stated on this bid.

Measurement of the diesel consumption. It shall be carried out a comparison between the previously recorded diesel consumption and the new measured consumption rates. The results shall be given to the Employer in form of a report.

## Documentation

The bid documentation shall describe the full system functionality, main system components, performance and parameters (data sheets), connection of existing equipment, redundancy principle, communication interfaces, the backup and recovery concepts for the EMS, anti-virus and malware protection, and shall include the software and hardware requirements for the proposed backup concept.

### Documentation to be submitted with Bid

The Bidder must complete all forms given in Section 4–- Bidding Forms of the Bidding Document for the BESS & EMS. All of them shall be submitted electronically as PDF, Excel or Word-file. Technical data sheets should be supplemented by additional descriptions, explanations, drawings and all other information necessary for a clear understanding of the bid to enable the Employer to undertake the necessary assessment, evaluation and verification of the technical and performance features of the bid.

In any case major deviations are discouraged and Employer reserves the right to reject any bid as noncompliant in his sole discretion.

The Bidder shall include the interface documents in his bid.

The Bidder shall include a list of his sub-contractors.

The Bidder shall submit a record of the executed projects in the power sector within the last 10 years.

The Bidder shall include the civil design criteria in his bid consisting of but not limited to corrosion protection plan, load bearing capacities of roads and bridges for truck traffic. The Bidder shall prepare a binding description of included furniture, equipment, appliances and the like together with the respective type of quality.

### Documentation to be submitted after contract award

The following describes the minimum scope of information, documents, drawings, etc. to be submitted by the successful Bidder to the Employer after award of contract during the design and engineering phase and during site construction of the BESS & EMS. The Employer reserves the right to request from the successful Bidder such additional information, drawings, documents, etc. as may be reasonably required for proper understanding and definition of the design and engineering of the project.

The successful Bidder shall provide four (4) copies of all drawings and documentation to be submitted by him. For the as-built documentation a well-organized electronic file including an Excel based table of contents, two (2) copies (plus electronic copy) shall be provided. All information with respect to connection points and interfaces between the Plant and the grid, and any other interface as well as for the entire BESS & EMS itself shall be included. The number of copies or the final content may be amended as may otherwise be required by the provisions of the Contract or as may otherwise be reasonably required by the Employer.

Bi-monthly status reports shall be provided by the successful bidder. Any revision of the project implementation schedule shall not be delivered later than seven (7) days after such revision.

### Documentation to be submitted during detail design

The following documents shall be submitted as a minimum by the successful Bidder to the Employer within a maximum of two (2) months after the date of contract award:

Detail design reports of all systems, buildings, and structures.

The Bidder shall hand-in his method statements for construction methods.

General arrangement and layout drawings

Project documents (data sheets, specifications, drawings) for major systems and components including system description of the main systems

Single line diagrams

Calculations and layouts for grounding, earthing, lightning protection, surge prevention

Cable list and cable size calculation

Soil resistivity measurement

Detailed layout drawings not limited to architectural, structural and electrical drawings.

Report of the design loads and load bearing capacities buildings and structures

Underground / aboveground ducts and cable arrangement drawings (civil and electrical)

Quality assurance philosophy

Information about corrosion protection for steel structures

Operation and maintenance philosophy

Emergency Response Plan

HSE plan

### Final Documentation

Before the final acceptance of the BESS and EMS the Contractor shall deliver to the Employer the final documentation, both in digital and hard copies (2x). The final documentation for the BESS shall be prepared in accordance with the IEC 62446 standard.

For the BESS and EMS, the final documentation shall comprise at least the following:

All As-built drawings (civil, mechanical, electrical) but not limited to:

SLD’s

Cable routing plans and calculations

Cable list

Substructure and module mounting details

Generator synchronizing panel and main distribution panel drawings

Data sheets of installed components

Warranties of installed components

O&M manuals

Site safety procedures

HSE procedure and plan

Test protocols

Performed studies and tests

Mechanical completion documents (not limited to):

Data sheets and manuals of components and equipment

Serial number of inverters, transformers, combiner boxes, etc.

Flash list of installed modules

Acceptance protocols

Calibration protocols

Factory Acceptance Test Reports for all mechanical and electrical equipment

Acceptance protocols between Contractor and Subcontractor

Commissioning protocols

Provisional Acceptance Certificate

Punch lists (Reserve lists) for the Defects Liability Period

Password for inverters, internal communication and SCADA system

## Training Program

The Bidder is required to provide training at manufacturer’s site for two persons from each powerhouse, two staff from FENAKA head office and two staff from PMU (total 10 persons). In addition, local staff should be given training on operation and maintenance during construction.

The training shall take one week on the manufacturer’s premises plus 24 days on the 2 construction sites for each team separate.

All living, accommodation, food, transport expenses of the trainees during the period of training/study tour including airfares, incidental expenses, medical expenses, medical insurances etc. will be covered by the Contractor including pocket allowance of US$100/day/person for training abroad. For the purposes of calculation, a day shall be considered for each night a participant is required to stay away from their usual place of residence.

The goal of the training and qualification program is to ensure that the BESS / EMS personnel acquire and maintain the combination of knowledge and demonstrated skills to full fill their responsibilities. Likewise, the Employer will acquire the knowledge required to full fill his responsibilities as plant owner during operation. This will reasonably assure that the plant is operated safely and efficiently, while also ensuring its long-term economic success.

The trained persons must subscribe in a list and sign, how many hours they have attended the training.

Every attendant must receive a training documentation/handbook, where the training subjects are documented in detail.

During implementation the Contractor shall train the Employer’s personnel. The training shall be split in a practical and a theoretical part.

For the practical part, the staff to be trained shall be involved in the building process of the power plant, in order to understand the overall system.

The practical part shall consist of 14 training days with a 2 hours session each day.

The theoretical part shall be 10 days with a 2 hours session each day.

The Bidder shall be flexible enough to adapt the content of the training to the state of knowledge of the attendees

The training shall comprise but not be limited to the following:

Technical basics and components of the BESS and EMS

General function of the BESS

Norms and standards

Health, Safety, and Environmental (HSE), First Aid

Control room daily work

Operation of EMS

Monitoring of BESS

Access to EMS

Fault detection

Action plan after fault detection

Preventive maintenance

Supervision and managing of corrective maintenance

Performance of first level corrective maintenance, such as the replacement of spare parts and / or spare inverters

Spare parts logistic and usage

Plant documentation

Monthly reporting

Communication with suppliers

Managing of insurance claims

Maintenance of green areas, internal paths

## Ongoing O&M and troubleshooting support

For the first two years from the date of commissioning of the projects (including defect liability period), the Contractor will be responsible to remotely monitor on a day-to-day basis the functioning and performance of all units of the BESS and EMS and submit a monthly performance report to the Owner. In case there is any fault, malfunctioning or unexpected low performance of any of the units of BESS or EMS the Contractor will immediately report the Owner and take necessary measures to rectify the same at the minimum possible time. The above-mentioned services for the first two years will be a part of the supply contract.

After initial support for two years as stated above, the Contractor will provide technical support to FENAKA for another 3 years to address any technical, functional and performance issues of any of the units of BESS or EMS. This requirement is mandatory but will not be part of the bid evaluation. The Contractor will depute competent technical personnel to jointly work with FENAKA personnel to address such issues to the satisfaction of the employer.

The Contractor will submit a separate quote for the above-mentioned services on per year basis for a duration of not less than 3 years after two years of operation of the systems.

## O&M Service Requirements during the initial two-year operation

### Plant operation and control

Bidder shall provide O&M services (no daily operation of the plant is required). The operation and control system of the plant system should not be limited to registration of data but should comprise functions for assessment and interpretation of operating conditions in particular in order to allow for remote diagnosis of errors.

Electrical load data, diesel engine data and the battery status (SOC) shall be acquired by the EMS and handled within data storage, protocol, reporting and monitoring. It is mandatory that the EMS shall retrieve all necessary data to ensure reliability and performance according to its intended purpose.

Bidder shall prepare monthly reports using the remote EMS regarding the operation of the plant including electricity production, efficiency, fuel consumption, and availability. Any maintenance performed during the month shall also be reported and the action taken described clearly.

Bidder shall perform a minimum quarterly periodic maintenance services and service reports.

Bidder may sub-contract the performance of parts or all of the services, subject to the approval of the Employer and on the basis that the Bidder remains fully liable for the performance of the sub- contracted obligations.

Moreover, Bidder shall liaise with the original equipment manufacturer to identify changes in the recommendations for the monitoring and maintenance of the equipment that constitutes the plant. Preventive maintenance requirements

The maintenance of the plant shall be based on the following operation, dispatching, and other requirements:

Maintenance activities for the plant affecting the power output shall take place outside the peak load periods, i.e., during the period of low power demand and low solar irradiation conditions (morning/ evening/ at night).

Maintenance of the plant shall be carried out at a minimum in accordance with the equipment manufacturers’ suggested maintenance requirements and the scheduling requirements of Employer and follow applicable standards and industry practices.

### BESS specific maintenance activities

The scope of work shall comprise of but not limited to the following activities:

Inspection and testing according to IEC 62932-2-2: 2020. In particular the inspection shall comprise the control and preventive maintenance of

Inverters

Junction boxes

Cabling

Cable terminations

transformers

Maintenance of the site including green areas, paths, cable servitudes etc.

Cleaning of battery cabinets

Battery module maintenance

Monitoring and maintaining Heating, Ventilation, and Air Conditioning (HVAC)

### Corrective maintenance requirements

For the first two years of operation of the hybrid plant, the Bidder is required to provide full corrective maintenance. Corrective maintenance means the repair or replacement of defective material and components.

Corrective maintenance activities shall be initiated as soon as a failure is detected. It shall always be ensured that the staff of the Employer is present and trained during each corrective maintenance activities.

If a failure will be detected, O&M personal shall initiate corrective maintenance measures within 6 hours after its occurrence.

The Bidder shall be responsible for maintaining and refilling the spare parts stock. An overview of the spare parts approach, major inspection, overhauls of equipment, and replacement program of equipment shall be provided, including:

Spare and wear parts and consumables necessary for the proper and continuing functioning of the plant during the Defect Liability Period (DLP)

Requirements and storage conditions for the spare and worn parts and consumables.

Replacement strategy, spare parts, and reaction periods for inverters for the first years after the provisional acceptance of the plant.

Furthermore, the Bidder shall manage all warranty cases including the dismantling, packaging, shipping and / or safe disposal of defective materials.

## Detailed scope of Maintenance

The Contractor shall provide routine and preventive maintenance schedules for the Employer’s approval and shall carry out all routine and preventive maintenance accordingly.

The Contractor shall perform periodic preventive maintenance required for BESS, and EMS in accordance with the recommendations of Original Equipment Manufacturers (or OEMs) and as per their OEM official O&M manuals.

The Contractor shall perform all breakdown maintenance and other maintenance in the Facility.

The Contractor shall provide the required spare parts, tools and tackles, and consumables required for comprehensive operation and maintenance of the facility. The Contractor shall make arrangements to procure required spare parts, or equipment/s as required, tools and equipment, required to operate and maintain the facility in accordance with the recommendations of individual original equipment manufacturers at his own cost.

A list of recommended spare parts shall be submitted by the Contractor at the beginning of services; however, the complete recommended spares will be in the scope of the Contractor only. In case any equipment or spares is not listed in the mandatory spares list but are required vitally for the operation of the plant, then the same shall be procured and provided by the Contractor without any additional cost implication to the Employer.

The Contractor shall employ only such personnel who are adequately qualified and experienced for operating and maintaining and troubleshooting BESS, and EMS.

The Contractor shall provide copies of all necessary documents including the following:

- Operation and maintenance manuals for all equipment

- Failure Analysis/history/troubleshooting details of all the equipment

- List of vendors indicating names and addresses for procurement of essential spare parts

- Root cause analysis report for any major failure

- Record of consumables / spare parts

The Contractor shall implement software updates to control and monitor the systems including EMS/BMS to meet the plant facility operating requirements.

The Contractor shall, at all times, allow and provide the Employer all necessary information for the operation of BESS and EMS full, free, unconditional, safe and complete access to the EMS.

The Contractor shall provide the training to the Employer’s personnel in relation to the operation of the complete facility.

The Contractor shall carry out the performance monitoring for the Facility (BESS and EMS) on a continuous basis and in case of any deviation, the Contractor shall perform the due diligence appropriately to find out the actual root cause of such deviation. Thereafter the corrective action required to mitigate such deviation shall be undertaken by the Contractor without any additional cost.

The Contractor should monitor the annual service package, manage/supervise/complete the scheduled routine maintenance, repair services and testing activities of the BESS and EMS and document all O&M services completed via an agreed methodology. It should update the records with preventive maintenance services and track any problems or warranty issues. Through the analysis of the maintenance records, it should organize the next interventions to maintain the physical state of all equipment supplied.

The Contractor should confirm availability and take any measures to secure operating instructions, warranties and performance guarantees, and other project documentation.

The Contractor shall specify safety features in the O&M manual under normal operation and under emergency situations. The Contractor shall provide clear safety instructions to regional/local personnel engaged by the Contractor as well as the Employer’s staff for safe handling of the equipment.

The Contractor must provide a description of all failure modes, failure impacts, and the failsafe philosophy and explain the safety principles and implementation scheme for each component of the Battery system.

Emergency Response procedures must be provided by the Contractor, detailing the recommended strategy to fight a battery fire, risk assessment for a thermal runaway event, and the necessary PPE for the Fire Fighters.

The Contractor shall submit a Hazardous material management plan, emergency response plan, decommission plan and disposal plan for Employer’s approval.

The Contractor shall clearly document and share with the Employer regarding the presence of all hazardous materials. The BESS shall be configured to prevent personal contact of hazardous material or environmental contamination due to hazardous materials. The BESS will include appropriate first aid equipment for contact with hazardous materials. All hazardous material shall have a clearly documented method of safe disposal.

The Contractor shall be responsible for the removal and disposal of equipment associated with the BESS system, as directed by the Employer, as and when during the 2 years O&M period.

## Spare parts, consumables and special tools

The Bidder shall provide all spares parts and consumables necessary for the correct functioning during the warranty period (two years) and for performing the necessary maintenance activities. All spare parts shall be directly interchangeable with the corresponding parts in the power plants and shall meet the requirements of the present specifications.

Spare parts comprise all disciplines (civil, mechanical, electrical and I&C works) and shall be in compliance with the corresponding Schedules in Section 4.

All the special tools and other equipment necessary for the overhaul, maintenance, and adjustment of the power plant facilities and equipment shall be included in the Bidder’s scope of supply.

# Environmental, Health and Safety Management Requirement

The bidder will implement all actions and responsibilities allocated to the contractors under the EMP (Annex 1) for the full duration of the contractor’s involvement in the project, ensuring adherence to all applicable national environment, health, safety, and labor laws and regulations in force at the time and ensuring adherence to ADB’s Safeguard Policy Statement (2009) and the related IFC Environment, Health and Safety (EHS) guidelines.

The bidder will ensure the feasibility studies and detailed designs reflect the EMP requirements; seeking to ensure the same or no worse impact than the design assessed in the IEE available at https://www.adb.org/projects/documents/mld-55191-001-iee.

The bidder will ensure adequate budget and staff resources are allocated to comply with and implement the contractor’s responsibilities under the EMP and to supervise and monitor the active construction site to protect the environment and ensure the health and safety of all workers and affected community. They will ensure a suitably qualified and experienced safeguards team has been appointed to undertake regular on-site supervision and monitoring activities before the commencement of works. Adequate health and safety supervision shall be conducted during construction to ensure the health and safety of all workers and local community; the environment officer and health and safety officer will be supported by full-time on-site EHS supervisor, and a full-time on-site Health and Safety steward.

The bidder will undertake and document a facilitated health and safety risk assessment considering all stages of the project, not just those stages the contractor is responsible for.

The bidder will prepare a Construction Environment Management Plan (CEMP) and a Construction Health and Safety Management Plan (CHSMP) both with sub-plans as specified in the EMP for review and approval by the Employer prior to the commencement of works – these documents will comprise the contractor’s Environmental, Health, and Safety Management Plan (EHSMP). The Environmental, Health, and Safety Management Plan (EHSMP) shall cover, but not be limited to the following standards:

- ISO 14001: Environmental Management System

- ISO 45001: Occupational Health and Safety (OH&S) Management System

- ISO 9001: Quality Management System

The bidder will ensure no site establishment or construction activity is to take place before the Employer has received and approved the detailed design and requisite contractor’s EHSMP (CEMP and CHSMP including all sub-plans).

The bidder will ensure that all construction workers including all formal and informal employees and subcontractors understand their responsibilities to implement the EMP and mitigate environmental impacts associated with pre-construction and construction activities. They will ensure attendance at EHS training provided by the Employer. They will provide and ensure attendance at EHS training for formal and informal construction workers and other personnel as required.

The bidder will adopt a zero-tolerance approach to OHS on the project, enforce all workers to comply with the OHS requirements of the EMP including the wearing of appropriate PPE on the construction site.

The bidder will support the Employer in undertaking ongoing public consultations and implementing the site-level GRM; in particular, the contractor’s GRM focals (safeguards team) shall thoroughly document details of complaints and make its best efforts to resolve the complaints at project site level; all this information is to be included in monthly reports to be submitted by the contractor to the Employer.

The bidder will undertake environmental monitoring as set out in the EMOP (Annex 1) for the duration of their involvement in the project and documenting qualitative and quantitative monitoring results.

The bidder will establish their own internal systems for monitoring and reporting their EMP implementation.

The bidder will attend monthly EHS meetings and submit monthly and quarterly environmental management reports per an agreed template to the Employer (these reports will be included as part of the contractor’s monthly progress reports), relating the work undertaken over the reporting period and documenting the environmental measures including monitoring activities that have been carried out, problems encountered, record data including near misses and incidents, grievances received, and follow-up actions that were taken (or will be taken) to correct the problems.

The bidder will inform the Employer immediately in case of any approved detailed design changes or unanticipated environmental impacts occurring during the project implementation stage, and as required, provide any information needed to the Employer to enable them to promptly update the IEE/EMP for clearance by ADB before any changes are implemented.

The bidder will inform the Employer within 24 hours in case of chance find or incident on site and providing within 48 hours an incident report with corrective action detailing how reoccurrence will be prevented.

The bidder will inform the Employer immediately in case of any non-compliance and help them to prepare as necessary a corrective action plan for clearance by the financier, the contractor is required to implement all necessary corrective action requested by the Employer to ensure the project remains in compliance with national regulatory requirements, ADB’s Safeguard Policy Statement (2009), the project’s loan covenants and EMP requirements.

Some of the environmental concerns envisaged for the project and its mitigation measures are mentioned in the IEE available at https://www.adb.org/projects/documents/mld-55191-001-iee:

- Disturbances to residential areas during construction will be minimised through scheduling times and use of equipment that minimises noise disturbances.

- Solid waste will be generated in the construction phase, including construction waste, packaging materials and other equipment. This can be mitigated by adopting a stage of recycling all materials to the highest extent possible and collecting and disposing of remaining wastes at appropriate waste disposal sites, all the while following national regulations. Waste burning on the Project site will not be allowed.

- Follow mitigations recommended in the EMP in transportation of oversized or heavy wind turbine components to reduce impacts on existing offsite wharfs/jetties, access roads, culverts, turning radii, public utilities and disturbances to general public.

- Ensure occupational and community health and safety risks of community and workers by following mitigation measures recommended in the EMP.

Impact on workers:

- Workers may be put at physical risk from electrical shocks, dust, handling heavy materials and equipment, falls and falling objects, work on slippery surfaces, and fire hazards; all of which will be present throughout the project construction period. Workers may come into contact with high-voltage power lines/equipment during operation, maintenance and repair. These impacts can be mitigated by implementing a good practice Occupational Health and Safety Plan (OHS Plan) including the use of Personal Protective Equipment (PPE) and Emergency Response Procedures (ERP), developed in compliance with relevant safety regulations.

- Project construction has the potential to cause disturbances in the community, such as public safety risks from construction activities, fires, spills of materials, and risks associated with unauthorized entry into work areas. These potential impacts can be mitigated by implementing good community health and safety practices, installation of site safety fencing and warning signs and, employing on-site supervision personnel (including night guards) as determined by the risk, to prevent unauthorized access to construction areas.

- In addition to the above, the contractor should follow the requirements of the provided Environmental Management Plan.

Schedule for monitoring and supervision:

The contractor shall prepare a periodic monitoring schedule which will ensure that management measures are being fulfilled to mitigate environmental and social impacts.  Monitoring will focus on the two key areas discussed below as well as those required under the Environmental Monitoring Plan attached in Annex 1.

Compliance Monitoring

- During the project preparation phase, compliance monitoring activities will focus on ensuring the effective implementation of the Environmental, Health, and Safety Management Plan.

- The environmental expert of the Contractor agency will ensure proper and timely conduct in compliance with the Environmental, Health, and Safety Management Plan.

- During the implementation phase, compliance monitoring would include inspections during the construction of the project’s components to verify the extent to which environmental authorization conditions and the EHSMP are being adhered to.

- The monitoring of environmental and social performance during project construction, operation and decommissioning will be the full responsibility of the Contractor.

Impact monitoring:

- It will be the ultimate responsibility of the Contractor to monitor and make sure that no violations take place at the site.

- The Environmental, Health, and Safety Management Plan (EHSMP) will form the basis for contractor activities at the project site to ensure that works proceed in accordance with established mitigation and management measures.

Arrangement for Reporting:

Monthly project environmental and social progress reports will be compiled as part of project performance reporting. Such environmental and social reporting would be integrated with overall project status and performance reporting. The reporting should include parameters required to be monitored by the Contractor as outlined in the Environmental Monitoring Plan in Annex 1.

Requirement for training and capacity building:

The Bidder will provide training to all the staff working on-site. This training program will focus on relevant environmental, health and safety laws, regulations and policies.

# Drawings

The bidder shall submit any drawing appropriate to help explain the solution provided.

# Certificates

## Form of Completion Certificate

Contract: [. . . . .insert name of contract and contract identification details.  . . . . ]

Date:

Certificate No.:

To:  [. . . . .insert name and address of contractor.  . . . . ]

Dear Ladies and/or Gentlemen,

Pursuant to GCC Clause 24 (Completion of the Facilities) of the General Conditions of the Contract entered into between yourselves and the Employer dated [. . . . .insert date. . . . . ], relating to the [. . . .brief description of the Facilities . . . .], we hereby notify you that the following part(s) of the Facilities was (were) complete on the date specified below, and that, in accordance with the terms of the Contract, the Employer hereby takes over the said part(s) of the Facilities, together with the responsibility for care and custody and the risk of loss thereof on the date mentioned below.

1.	Description of the Facilities or part thereof:  [. . . .description . . . .]

2.	Date of Completion:  [. . . .date . . . .]

However, you are required to complete the outstanding items listed in the attachment hereto as soon as practicable.

This letter does not relieve you of your obligation to complete the execution of the Facilities in accordance with the Contract nor of your obligations during the Defect Liability Period.

Very truly yours,

[. . . .Signature . . . .]

Project Manager

## Form of Operational Acceptance Certificate

Contract: [. . . . .insert name of contract and contract identification details.  . . . . ]

Date:

Certificate No.:

To:  [. . . . .insert name and address of contractor.  . . . . ]

Pursuant to GCC Subclause 25.3 (Operational Acceptance) of the General Conditions of the Contract entered into between yourselves and the Employer dated [. . .date. . .], relating to the [. . .brief description of the facilities. . .], we hereby notify you that the Functional Guarantees of the following part(s) of the Facilities were satisfactorily attained on the date specified below.

1.	Description of the Facilities or part thereof:  [. . . description . . .]

2.	Date of Operational Acceptance:  [. . . date . . .]

This letter does not relieve you of your obligation to complete the execution of the Facilities in accordance with the Contract nor of your obligations during the Defect Liability Period.

Very truly yours,

[. . . .Signature . . . .]

Project Manager

# Change Orders

## Change order procedure

### General

This section provides samples of procedures and forms for implementing changes in the Facilities during the performance of the Contract in accordance with GCC Clause 39 (Change in the Facilities) of the General Conditions.

### Change Order Log

The Contractor shall keep an up-to-date Change Order Log to show the current status of Requests for Change and Changes authorized or pending. Entries of the Changes in the Change Order Log shall be made to ensure that the log is up-to-date. The Contractor shall attach a copy of the current Change Order Log in the monthly progress report to be submitted to the Employer.

### References for Changes

(1) Request for Change as referred to in GCC Clause 39 shall be serially numbered CR-X-nnn.

(2) Estimate for Change Proposal as referred to in GCC Clause 39 shall be serially numbered CN-X-nnn.

(3) Acceptance of Estimate as referred to in GCC Clause 39 shall be serially numbered CA-X-nnn.

(4) Change Proposal as referred to in GCC Clause 39 shall be serially numbered CP-X-nnn.

(5) Change Order as referred to in GCC Clause 39 shall be serially numbered CO-X-nnn.

Note:

(a)	Requests for Change issued from the Employer’s Home Office and the Site representatives of the Employer shall have the following respective references:

Home Office	CR-H-nnn

Site	CR-S-nnn

(b)	The above number “nnn” is the same for Request for Change, Estimate for Change Proposal, Acceptance of Estimate, Change Proposal and Change Order.

## Change Order Forms

### Request for Change Proposal Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

With reference to the captioned Contract, you are requested to prepare and submit a Change Proposal for the Change noted below in accordance with the following instructions within [  number  ] days of the date of this letter [or on or before (  date  )].

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Number  ]

3.	Originator of Change:

Employer:  [Name]

Contractor (by Application for Change Proposal No. [Number Refer to Annex 6.2.7])

4.	Brief Description of Change:  [  Description  ]

5.	Facilities and/or Item No. of equipment related to the requested Change:  [  Description  ]

6.	Reference drawings and/or technical documents for the request of Change:

Drawing No./Document No.		Description

7.	Detailed conditions or special requirements on the requested Change:  [  Description  ]

8.	General Terms and Conditions:

(a)	Please submit your estimate showing what effect the requested Change will have on the Contract Price.

(b)	Your estimate shall include your claim for the additional time, if any, for completing the requested Change.

(c)	If you have any opinion that is critical to the adoption of the requested Change in connection with the conformability to the other provisions of the Contract or the safety of the Plant or Facilities, please inform us in your proposal of revised provisions.

(d)	Any increase or decrease in the work of the Contractor relating to the services of its personnel shall be calculated.

(e)	You shall not proceed with the execution of the work for the requested Change until we have accepted and confirmed the amount and nature in writing.

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

### Estimate for Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

With reference to your Request for Change Proposal, we are pleased to notify you of the approximate cost to prepare the below-referenced Change Proposal in accordance with GCC Subclause 39.2.1 of the General Conditions.  We acknowledge that your agreement to the cost of preparing the Change Proposal, in accordance with GCC Subclause 39.2.2, is required before estimating the cost for change work.

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Number  ]

3.	Brief Description of Change:  [  Description  ]

4.	Scheduled Impact of Change:  [  Description  ]

5.	Cost for Preparation of Change Proposal:  [  insert costs, which shall be in the currencies of the contract  ]

(a)	Engineering	(Amount)

(i)	Engineer		 hours (hrs) x 	 rate/hr =

(ii)	Draftsperson		 hrs x 	 rate/hr =

Sub-total		 hrs

Total Engineering Cost

(b)	Other Cost

Total Cost (a) + (b)

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

### Acceptance of Estimate Form

[ Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [ Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We hereby accept your Estimate for Change Proposal and agree that you should proceed with the preparation of the Change Proposal.

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Request number/revision  ]

3.	Estimate for Change Proposal No./Rev.:  [  Proposal number/revision  ]

4.	Acceptance of Estimate No./Rev.:  [  Estimate number/revision  ]

5.	Brief Description of Change:  [  Description  ]

6.	Other Terms and Conditions:  In the event that we decide not to order the Change accepted, you shall be entitled to compensation for the cost of preparing the Change Proposal described in your Estimate for Change Proposal mentioned in para. 3 above in accordance with GCC Clause 39 of the General Conditions.

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

### Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

In response to your Request for Change Proposal No. [Number], we hereby submit our proposal as follows:

1.	Title of Change:  [  Name  ]

2.	Change Proposal No./Rev.:  [  Proposal number / revision ]

3.	Originator of Change:	Employer:  [ Name  ] / Contractor:  [  Name  ]

4.	Brief Description of Change:  [  Description  ]

5.	Reasons for Change:  [  Reason  ]

6.	Facilities and/or Item No. of Equipment related to the requested Change:  [  Facilities  ]

7.	Reference drawings and/or technical documents for the requested Change:

[  Drawing/Document No./Description  ]

8.	Estimate of increase/decrease to the Contract Price resulting from the Change Proposal:

Amount

[ insert  amounts in the currencies of the Contract ]

(a)	Direct material

(b)	Major construction equipment

(c)	Direct field labor (Total 	 hrs)

(d)	Subcontracts

(e)	Indirect material and labor

(f)	Site supervision

(g)	Head office technical staff salaries

Process engineer		 hrs @ 	 rate/hr

Project engineer		 hrs @ 	 rate/hr

Equipment engineer		 hrs @ 	 rate/hr

Procurement		 hrs @ 	 rate/hr

Draftsperson		 hrs @ 	  rate/hr

Total			hrs

(h)	Extraordinary costs (computer, travel, etc.)

(i)	Fee for general administration, 	 % of Items

(j)	Taxes and customs duties

Total lump sum cost of Change Proposal		[  Sum of items (a) to (j)  ]

Cost to prepare Estimate for Change Proposal	 [  Amount payable if Change is not accepted  ]

9.	Additional time for Completion required due to Change Proposal

10.	Effect on the Functional Guarantees

11.	Effect on the other terms and conditions of the Contract

12.	Validity of this Proposal:  within [Number] days after receipt of this Proposal by the Employer

13.	Other terms and conditions of this Change Proposal:

(a)	You are requested to notify us of your acceptance, comments or rejection of this detailed Change Proposal within [Number] days from your receipt of this Proposal.

(b)	The amount of any increase and/or decrease shall be taken into account in the adjustment of the Contract Price.

(c)	Contractor’s cost for preparation of this Change Proposal: [ . . . .insert amount. This cost shall be reimbursed by the employer in case of employer’s withdrawal or rejection of this Change Proposal without default of the contractor in accordance with GCC Clause 39 of the General Conditions . . . . ]

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

### Change Order Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We approve the Change Order for the work specified in the Change Proposal (No. [  number  ]), and agree to adjust the Contract Price, Time for Completion, and/or other conditions of the Contract in accordance with GCC Clause 39 of the General Conditions.

1.	Title of Change:  [  Name  ]

2.	Change Request No./Rev.:  [  Request number / revision  ]

3.	Change Order No./Rev.:  [  Order number / revision  ]

4.	Originator of Change:	Employer:  [Name] / Contractor:  [  Name  ]

5.	Authorized Price:

Ref. No.:  [  Number  ]	Date:  [  Date  ]

Foreign currency portion [  Amount  ]  plus Local currency portion [  Amount  ]

6.	Adjustment of Time for Completion

None		Increase [  Number  ] days	 	Decrease [  Number  ] days

7.	Other effects, if any

Authorized by:  		Date:

Employer

Accepted by:  		Date:

Contractor

### Pending Agreement Change Order Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We instruct you to carry out the work in the Change Order detailed below in accordance with GCC Clause 39 of the General Conditions.

1.	Title of Change:  [  Name  ]

2.	Employer’s Request for Change Proposal No./Rev.:  [  number/revision  ]	dated:  [ date  ]

3.	Contractor’s Change Proposal No./Rev.:  [  number / revision  ]	dated:  [ date ]

4.	Brief Description of Change:  [ Description ]

5.	Facilities and/or Item No. of equipment related to the requested Change:  [ Facilities ]

6.	Reference Drawings and/or technical documents for the requested Change:

[  Drawing / Document No. / Description  ]

7.	Adjustment of Time for Completion:

8.	Other change in the Contract terms:

9.	Other terms and conditions:

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

### Application for Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We hereby propose that the work mentioned below be treated as a Change in the Facilities.

1.	Title of Change:  [  Name  ]

2.	Application for Change Proposal No./Rev.:  [  Number / revision  ]	dated:  [  Date  ]

3.	Brief Description of Change:  [  Description  ]

4.	Reasons for Change:

5.	Order of Magnitude Estimation (amount in the currencies of the Contract): [  Amount  ]

6.	Scheduled Impact of Change:

7.	Effect on Functional Guarantees, if any:

8.	Appendix:

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

# Personnel Requirements

Using Form PER-1 and PER-2 in Section 4 (Bidding Forms), the Bidder must demonstrate that it has personnel who meet the following requirements:

| No. | Position | Total Work Experience [years] | Experience In Similar Work [years] |  |
| --- | --- | --- | --- | --- |
| 1 | Project Manager (Electrical Engineer) | 15 | 7 |  |
| 2 | EMS Specialist | 10 | 5 |  |
| 3 | BESS Specialist | 10 | 5 |  |
| 4 | Electrical Engineer | 10 | 5 |  |
| 5 | Environment, Health and Safety Expert related to electrical and BESS | 10 | 5 |  |
| 6 |  | Construction Engineer (civil and cabling) | 7 | 3 |

All staff must be fluent in English.

# Equipment Requirements

Using Form EQU in Section 4 (Bidding Forms), the Bidder must demonstrate that it has the key equipment listed below:

| No. | Equipment Type and Characteristics | Minimum Number Required |
| --- | --- | --- |
| 1 | Crane to move and place the containers | 1 per site |
| 2 |  |  |
| 3 |  |  |

# Annex 1. Environmental Management Plan

The environmental management plan includes the implementation arrangements, mitigation measures and monitoring requirements given in Chapter VII, Appendix 16 and Appendix 17 (given below) of the Initial Environmental Examination (IEE) for the ASSURE project and also available at https://www.adb.org/projects/documents/mld-55191-001-iee.

This EMP will form part of the contract document together with General Environment, Health & Safety (EHS) Conditions of Contract (CoC) for all contractors.

This EMP will form the basis for the contractor to prepare their environmental, health and safety management plan and the Construction Environment Management Plan (CEMP).