# Republic of Maldives

Request for Proposals

Design, Build and Operation of 10MLD Sewage Treatment Plant in Hulhumalé Phase 1

(Single—stage (Two Envelop RFP)

Project: Maldives Urban development and Resilience Project

Country: Republic of Maldives

Credit No. / Grant No.: No-6537-MV/No-D554-MV

RFP No: MV-MONPI-223416-CW-RFP

Issued on: July, 2021

Issued by: National Tender, Ministry of Finance

Table of Content

PART 1 – Request for Proposal Procedures	3

Section I – Instructions to Proposers (ITP)	4

Section II – Proposal Data Sheet (PDS)	37

Section III – Evaluation and Qualification Criteria	48

Section IV – Proposal Forms	55

Section V – Eligible Countries	110

Section VI – Fraud and Corruption	111

PART 2 – Employer’s Requirements	113

Section VII – Employer’s Requirements	114

PART 3 – Conditions of Contract and Contract Forms	131

Section VIII – General Conditions (GC)	132

Section IX – Particular Conditions (PC)	133

Section X – Contract Forms	194

PART 1 – Request for Proposal Procedures

Section I – Instructions to Proposers (ITP)

Table of Content

A. General	6

1. Scope of Proposal	6

2. Source of Funds	7

3. Fraud and Corruption	7

4. Eligible Proposers	8

5. Eligible Materials, Equipment, and Services	11

B. Contents of RFP Document	11

6. Sections of RFP Document	11

7. Clarification of RFP Document, Site Visit, Pre-Proposal Meeting	12

8. Amendment of RFP Document	13

9. Cost of Proposals	13

10. Contacting the Employer	13

11. Language of Proposals	13

C. Preparation of Proposals	13

12. Documents Comprising the Proposal	13

13. Letter of Proposal, and Schedules	15

14. Alternative Technical Proposals	15

15. Proposal Prices	16

16. Proposal Currencies	17

17. Documents Establishing the Qualification of the Proposer	17

18. Documents Establishing Conformity of the Works	18

19. Securing the Proposal	18

20. Period of Validity of Proposals	20

21. Format and Signing of Proposal	21

D. Submission of Proposals	21

22. Submission, Sealing and Marking of Proposals	21

23. Deadline for Submission of Proposals	22

24. Late Proposals	22

25. Withdrawal, Substitution, and Modification of Proposals	23

E. Opening of Technical Parts of Proposals	24

26. Opening of Technical Part by Employer	24

F. Evaluation of Proposals – General Provisions	25

27. Confidentiality	25

28. Clarification of Proposals	25

29. Deviations, Reservations, and Omissions	25

G. Evaluation of Technical Parts of Proposals	26

30. Determination of Responsiveness of Technical Parts	26

31. Evaluation of Technical Parts	26

32. Evaluation of Proposer’s Qualification	27

33. Notification of evaluation of Technical Parts	27

H. Opening of Financial Parts	28

34. Public Opening of Financial Parts when BAFO or negotiations do not apply	28

35. Opening of Financial Parts when BAFO or negotiations apply	28

I. Evaluation of Financial Part	29

36. Nonmaterial Nonconformities	29

37. Arithmetic Correction	29

38. Conversion to Single Currency	30

39. Margin of Preference	30

40. Evaluation Process Financial Parts	30

41. Abnormally Low Proposals	31

42. Unbalanced or Front Loaded Proposals	31

J. Evaluation of Combined Technical and Financial Part	32

43. Evaluation of Combined Technical and Financial Parts	32

44. Best and Final Offer (BAFO)	32

45. Most Advantageous Proposal (MAP)	32

46. Negotiations	32

47. Employer’s Right to Accept Any Proposal, and to Reject Any or All Proposals	33

48. Standstill Period	33

49. Notification of Intention to Award	33

K. Award of Contract	34

50. Award Criteria	34

51. Notification of Award	34

52. Debriefing by the Employer	35

53. Signing of Contract	35

54. Performance Security	35

55. Procurement Related Complaint	36

# Section I – Instructions to Proposers

A. General

| - Scope of Proposal | - The Employer, as specified in the Proposal Data Sheet (PDS), issues this Request for Proposals (RFP) Document for the design, build and operation of the Works as specified in Section VII, Employer’s Requirements. The name, identification and number of lots (contracts) of this RFP are specified in the PDS. - Unless otherwise stated, throughout this RFP Document definitions and interpretations shall be as prescribed in the Section VIII, General Conditions. - Throughout this RFP Document: - the term “in writing” means communicated in written form (e.g. by mail, e-mail, fax, including if specified in the PDS, distributed or received through the electronic-procurement system used by the Employer) with proof of receipt; - if the context so requires, “singular” means “plural” and vice versa; - “Day” means calendar day, unless otherwise specified as “Business Day”. A Business Day is any day that is an official working day of the Borrower. It excludes the Borrower’s official public holidays; - “Operation Service” means the operation and maintenance of the Works as provided under the Contract; - “Works” refers to Works, subject of this request for proposals document, to be designed and built under the Contract; - “ES” means environmental and social (including Sexual Exploitation and Abuse (SEA), and Sexual Harassment (SH)); - “Sexual Exploitation and Abuse” “(SEA)” means the following: Sexual Exploitation is defined as any actual or attempted abuse of position of vulnerability, differential power or trust, for sexual purposes, including, but not limited to, profiting monetarily, socially or politically from the sexual exploitation of another. Sexual Abuse is defined as the actual or threatened physical intrusion of a sexual nature, whether by force or under unequal or coercive conditions; - “Sexual Harassment” “(SH)” is defined as unwelcome sexual advances, requests for sexual favors, and other verbal or physical conduct of a sexual nature by the Contractor’s Personnel with other Contractor’s or Employer’s Personnel; - “Contractor’s Personnel” is as defined in Sub-Clause 1.1.21 of the General Conditions; and - “Employer’s Personnel” is as defined in Sub-Clause 1.1.34 of the General Conditions. A non-exhaustive list of (i) behaviors which constitute SEA and (ii) behaviors which constitute SH is attached to the Code of Conduct form in Section IV. |
| --- | --- |
| - Source of Funds | - The Borrower or Recipient (hereinafter called “Borrower”) indicated in the PDS has applied for or received financing (hereinafter called “funds”) from the International Bank for Reconstruction and Development or the International Development Association (hereinafter called “the Bank”) in an amount specified in the PDS toward the project named in the PDS. The Borrower intends to apply a portion of the funds to eligible payments under the contract(s) for which this RFP Document is issued. - Payments by the Bank will be made only at the request of the Borrower and upon approval by the Bank in accordance with the terms and conditions of the Loan (or other financing) Agreement between the Borrower and the Bank (hereinafter called the Loan Agreement), and will be subject in all respects to the terms and conditions of that Loan (or other financing) Agreement. The Loan (or other financing) Agreement prohibits a withdrawal from the loan account for the purpose of any payment to persons or entities, or for any import of equipment, materials or any other goods, if such payment or import is prohibited by a decision of the United Nations Security Council taken under Chapter VII of the Charter of the United Nations. No party other than the Borrower shall derive any rights from the Loan (or other financing) Agreement or have any claim to the proceeds of the Loan (or other financing). |
| - Fraud and Corruption | - The Bank requires compliance with the Bank’s Anti-Corruption Guidelines and its prevailing sanctions policies and procedures as set forth in the WBG’s Sanctions Framework, as set forth in Section VI. - In further pursuance of this policy, Proposers shall permit and shall cause their agents (where declared or not), subcontractors, sub-consultants, service providers, suppliers, and personnel, to permit the Bank to inspect all accounts, records and other documents relating to any initial selection process, prequalification process, ,proposal submission and contract performance (in the case of award), and to have them audited by auditors appointed by the Bank. |
| - Eligible Proposers | - A Proposer may be a firm that is a private entity, a state-owned enterprise or institution subject to ITP 4.6, or any combination of such entities in the form of a joint venture (JV) under an existing agreement or with the intent to enter into such an agreement supported by a letter of intent. In the case of a joint venture, all members shall be jointly and severally liable for the execution of the Contract in accordance with the Contract terms. The JV shall nominate a Representative (Lead Member) who shall have the authority to conduct all business for and on behalf of any and all the members of the JV during the RFP process and, in the event the JV is awarded the Contract, during contract execution. Unless specified in the PDS, there is no limit on the number of members in a JV. If specified in the PDS, the JV may form an SPV to enter into the Contract and the minimum level of total paid up share capital, lock-in periods for members maintaining their shares and extent to which members can dilute their shareholding shall be as specified in the PDS. - A Proposer shall not have a conflict of interest. Any Proposer found to have a conflict of interest shall be disqualified. A Proposer may be considered to have a conflict of interest for the purpose of this RFP process, if the Proposer: - directly or indirectly controls, is controlled by or is under common control with another Proposer; or - receives or has received any direct or indirect subsidy from another Proposer; or - has the same legal representative as another Proposer; or - has a relationship with another Proposer, directly or through common third parties, that puts it in a position to influence the Proposal of another Proposer, or influence the decisions of the Employer regarding this RFP process; or - any of its affiliates participates as a consultant in the preparation of the Employer’s Requirements for the Works that are the subject of the Proposal; or - or any of its affiliates has been hired (or is proposed to be hired) by the Employer or Borrower as the Employer’s Representative for the Contract implementation; or - would be providing goods, works, or non-consulting services resulting from or directly related to consulting services for the preparation or implementation of the project specified in the PDS ITP 2.1 that it provided or were provided by any affiliate that directly or indirectly controls, is controlled by, or is under common control with that firm; or - has a close business or family relationship with a professional staff of the Borrower (or of the project implementing agency, or of a recipient of a part of the loan) who: (i) are directly or indirectly involved in the preparation of the RFP Document or specifications of the Contract, and/or the Proposal evaluation process of such Contract; or (ii) would be involved in the implementation or supervision of such Contract unless the conflict stemming from such relationship has been resolved in a manner acceptable to the Bank throughout the RFP process and execution of the Contract. - A firm that is a Proposer (either individually or as a JV member) shall not participate in more than one Proposal, except for permitted alternative Proposals. This includes participation as a subcontractor in other Proposals. Such participation shall result in the disqualification of all Proposals in which the firm is involved. A firm that is not a Proposer or a JV member may participate as a subcontractor in more than one Proposal. - A Proposer may have the nationality of any country, subject to the restrictions pursuant to ITP 4.8. A Proposer shall be deemed to have the nationality of a country if the Proposer is constituted, incorporated or registered in and operates in conformity with the provisions of the laws of that country, as evidenced by its articles of incorporation (or equivalent documents of constitution or association) and its registration documents, as the case may be. This criterion also shall apply to the determination of the nationality of proposed sub-contractors or sub-consultants for any part of the Contract including related Services. - A Proposer that has been sanctioned by the Bank, pursuant to the Bank’s Anti-Corruption Guidelines, and in accordance with its prevailing sanctions policies and procedures as set forth in the WBG’s Sanctions Framework as described in Section VI paragraph 2.2 d., shall be ineligible to be initially selected for, prequalified for, Proposal for, submit proposal for, or be awarded a Bank-financed contract or benefit from a Bank-financed contract, financially or otherwise, during such period of time as the Bank shall have determined. The list of debarred firms and individuals is available at the electronic address specified in the PDS. - Proposers that are state-owned enterprises or institutions in the Employer’s Country may be eligible to compete and be awarded a Contract(s) only if they can establish, in a manner acceptable to the Bank, that they (i) are legally and financially autonomous (ii) operate under commercial law, and (iii) are not under supervision of the Employer. - A Proposer shall not be under suspension from submitting proposals by the Employer as the result of the operation of a Proposal or Proposal–Securing Declaration. - Firms and individuals may be ineligible if so indicated in Section V and (a) as a matter of law or official regulations, the Borrower’s country prohibits commercial relations with that country, provided that the Bank is satisfied that such exclusion does not preclude effective competition for the supply of goods or the contracting of works or services required; or (b) by an act of compliance with a decision of the United Nations Security Council taken under Chapter VII of the Charter of the United Nations, the Borrower’s country prohibits any import of goods or contracting of works or services from that country, or any payments to any country, person, or entity in that country. When the procurement is implemented across jurisdictional boundaries (and more than one country is a Borrower, and is involved in the procurement), then exclusion of a firm or individual on the basis of ITP 4.8 (a) above by any country may be applied to that procurement across other countries involved, if the Bank and the Borrowers involved in the procurement agree. - A Proposer shall provide such documentary evidence of eligibility satisfactory to the Employer, as the Employer shall reasonably request. - A firm that is under a sanction of debarment by the Borrower from being awarded a contract is eligible to participate in this procurement, unless the Bank, at the Borrower’s request, is satisfied that the debarment; (a) relates to fraud or corruption, and (b) followed a judicial or administrative proceeding that afforded the firm adequate due process. |
| - Eligible Materials, Equipment, and Services | - The materials, equipment and services to be supplied under the Contract may have their origin in any country subject to the restrictions specified in Section V, Eligible Countries, and all expenditures under the Contract will not contravene such restrictions. At the Employer’s request, Proposers may be required to provide evidence of the origin of materials, equipment and services. |

B. Contents of RFP Document

| - Sections of RFP Document | - The RFP Document consists of Parts 1, 2, and 3, which include all the sections indicated below, and should be read in conjunction with any Addenda issued in accordance with ITP 8: PART 1 Request for Proposal Procedures Section I - Instructions to Proposers (ITP) Section II - Proposal Data Sheet (PDS) Section III - Evaluation and Qualification Criteria Section IV - Proposal Forms Section V - Eligible Countries Section VI - Fraud and Corruption PART 2 Employer’s Requirements Section VII - Employer’s Requirements PART 3 Conditions of Contract and Contract Forms Section VIII - General Conditions Section IX - Particular Conditions Section X - Contract Forms - The Specific Procurement Notice, Notice of Request for Proposals (RFP) issued by the Employer, is not part of this RFP Document. - Unless obtained directly from the Employer, the Employer is not responsible for the completeness of the document, responses to requests for clarification, the Minutes of the pre-Proposal meeting (if any), or Addenda to the RFP Document in accordance with ITP 8. In case of any contradiction, documents obtained directly from the Employer shall prevail. - The Proposer is expected to examine all instructions, forms, terms, and specifications in the RFP Document and to furnish with its Proposal all information or documentation as is required by the RFP Document. |
| --- | --- |
| - Clarification of RFP Document, Site Visit, Pre-Proposal Meeting | - A Proposer requiring any clarification of the RFP Document shall contact the Employer in writing at the Employer’s address specified in the PDS or raise its enquiries during the pre-Proposal meeting if provided for in accordance with ITP 7.4. The Employer will respond to any request for clarification, provided that such request is received prior to the deadline for submission of Proposals within a period specified in the PDS. The Employer shall forward copies of its response to all Proposers who have acquired the RFP Document in accordance with ITP 6.3, including a description of the inquiry but without identifying its source. If so specified in the PDS, the Employer shall also promptly publish its response at the web page identified in the PDS. Should the Employer deem it necessary to amend the RFP Document as a result of a request for clarification, it shall do so following the procedure under ITP 8. - The Proposer is advised to visit and examine the Site of the Works and its surroundings and obtain for itself on its own responsibility all information that may be necessary for preparing the Proposal and entering into a contract. The costs of visiting the site shall be at the Proposer’s own expense. - The Proposer and any of its personnel or agents will be granted permission by the Employer to enter upon its premises and lands for the purpose of such visit, but only upon the express condition that the Proposer, its personnel, and agents will release and indemnify the Employer and its personnel and agents from and against all liability in respect thereof, and will be responsible for death or personal injury, loss of or damage to property, and any other loss, damage, costs, and expenses incurred as a result of the inspection. - The Proposer’s designated representative is invited to attend a pre-Proposal meeting and/or a site visit, if provided for in the PDS. The purpose of the meeting will be to clarify issues and to answer questions on any matter that may be raised at that stage. Nonattendance at the pre-Proposal meeting will not be a cause for disqualification of a Proposer. - The Proposer is requested to submit any questions in writing, to reach the Employer not later than one week before the meeting. - Minutes of the pre-Proposal meeting, including the text of the questions raised without identifying the source, and the responses given, together with any responses prepared after the meeting, will be transmitted promptly to all Proposers who have acquired the RFP Document in accordance with ITP 6.3. Any modification to the RFP Document that may become necessary as a result of the pre-Proposal meeting shall be made by the Employer exclusively through the issue of an Addendum pursuant to ITP 8 and not through the minutes of the pre-Proposal meeting. |
| - Amendment of RFP Document | - At any time prior to the deadline for submission of Proposals, the Employer may amend the RFP Document by issuing addenda. - Any addendum issued shall be part of the RFP Document and shall be communicated in writing to all who have obtained the RFP Document from the Employer in accordance with ITP 6.3. The Employer shall also promptly publish the addendum on the Employer’s web page in accordance with ITP 7.1. - To give prospective Proposers reasonable time in which to take the addendum into account in preparing their Proposals, the Employer may, at its discretion, extend the deadline for the submission of Proposals, pursuant to ITP 23.2. |
| - Cost of Proposals | - The Proposer shall bear all costs associated with the preparation and submission of its Proposal, and the Employer will in no case be responsible or liable for those costs. |
| - Contacting the Employer | - From the time of Proposal opening to the time of Contract award, if any Proposer wishes to contact the Employer on any matter related to the Proposal, it should do so in writing. - If a Proposer tries to directly influence the Employer or otherwise interfere in the Proposal evaluation process and the Contract award decision, its Proposal may be rejected. |
| - Language of Proposals | - Unless otherwise specified in the PDS, the Proposal prepared by the Proposer and all correspondence and documents related to the Proposal exchanged by the Proposer and the Employer shall be written in the English Language, or, if the PDS so provides, in either one of two languages specified there. Any printed literature furnished by the Proposer as part of its Proposal may be in a language not specified in the PDS, as long as such literature is accompanied by a translation of its pertinent passages into the language of the Proposal, in which case, for purposes of interpretation of the Proposal, the translation shall govern. |

C. Preparation of Proposals

| - Documents Comprising the Proposal | - The Proposal shall comprise two Parts, namely the Technical Part and the Financial Part. These two Parts shall be submitted simultaneously in two separate sealed envelopes (single-stage, two-envelope RFP process). One envelope shall contain only information relating to the Technical Part and the other, only information relating to the Financial Part. These two envelopes shall be enclosed in a separate sealed outer envelope marked “Original Proposal”. - The Technical Part of the Proposal submitted by the Proposer shall comprise the following: - Letter of Proposal - Technical Part, prepared in accordance with ITP 13; - Security: Proposal Security or Proposal-Securing declaration, in accordance with ITP 19; - Alternative Proposal - Technical Part, if permissible in accordance with ITP 14; - written confirmation authorizing the signatory of the Proposal to commit the Proposer, in accordance with ITP 21.1; - documentary evidence that the Proposer continues to be eligible and qualified to perform the contract if its Proposal is accepted; - documentary evidence in accordance with ITP 18 that the Works offered by the Proposer conform to the RFP Document; - method statements, equipment, personnel, schedule and any other information as stipulated in Section IV, Proposal Forms; - Details of any departures in their Technical Part from the RFP docuemnts; - in the case of a Technical Part submitted by a JV, JV agreement, or letter of intent to enter into a JV including a draft agreement, indicating at least the parts of the Works to be executed by the respective partners; - list of subcontractors, in accordance with ITP 18.3; and - any other document required in the PDS. - The Financial Part of the Proposal submitted by the Proposer shall comprise the following: - Letter of Proposal - Financial Part prepared in accordance with ITP 13; - Schedule of Rates and Prices (if any): completed in accordance with ITP 15 and ITP 16; - Alternative Proposal – Financial Part: if permissible in accordance with ITP 14; - Financial Disclosure: The Proposer shall furnish in the Letter of Proposal information on commissions and gratuities, if any, paid or to be paid to agents or any other party relating to this Proposal; and - Other: any other document required in the PDS. - The Technical Part shall not include any financial information related to the Proposal price. Where material financial information related to the Proposal price is contained in the Technical Part, the Proposal shall be declared non-responsive. - The Proposer shall furnish in the Letter of Proposal: Technical Part three names of the potential Dispute Adjudication Board (DAB) members and attach their curriculum vitae. The list of potential DAB members proposed by the Employer (Contract Data 20.3) and by the Proposer (Letter of Proposal) shall be subject to Bank’s No-objection. |
| --- | --- |
| - Letter of Proposal, and Schedules | - The Proposer shall complete the Letter of Proposal – Technical Part and Letter of Proposal - Financial Part using the relevant forms furnished in Section IV, Proposal Forms. The forms must be completed without any alterations to the text, and no substitutes shall be accepted except as provided under ITP 21.3. All blank spaces shall be filled in with the information requested. |
| - Alternative Technical Proposals | - Alternative Proposal - Technical Part: the Proposer wishing to offer alternative technical Proposal shall (i) document that the proposed technical alternatives are to the benefit of the Employer, that they fulfill the principal objectives of the contract, and that they meet the basic performance and technical criteria specified in the RFP Documents; and (ii) further provide all information necessary for a complete technical evaluation of the alternative by the Employer, including as relevant drawings, design calculations, technical specifications, and proposed construction methodology and other relevant details. - Alternative Proposal - Financial Part: The Proposer submitting alternative technical Proposal shall provide all information necessary for a complete financial evaluation of the alternative by the Employer, including breakdown of prices relevant to the offered technical alternative and in the manner and detail called for in the Schedule of Rates and Prices (if any) incuded in Section IV – Proposal Forms. - Only the technical alternatives, if any, of the Proposer with the Most Advantageous Proposal conforming to the basic performance and technical criteria specified in the RFP Documents shall be considered by the Employer. |
| - Proposal Prices | - Unless otherwise specified in the PDS, Proposers shall quote for the entire Works and Operation Service on a “single responsibility” basis such that the total lump sum Proposal price, subject to any adjustments in accordance with the Contract, covers all the Contractor’s obligations mentioned in or to be reasonably inferred from the RFP Document in respect of the design, manufacture, including procurement and subcontracting (if any), delivery, construction and completion of the Works and operation and maintenance of the Works as set out in the Conditions. This includes all requirements under the Contractor’s responsibilities for testing, pre-commissioning and commissioning (as applicable) of the Works and, where so required by the RFP Document, the acquisition of all permits, approvals and licenses, etc.; the operation, maintenance and training services and such other items and services as may be specified in the RFP Document, all in accordance with the requirements of the General Conditions. - Proposers shall give a breakdown of the prices in the manner and detail called for in the Schedule of Priced Activities and Sub-activities included in Section IV, Proposal Forms with further breakdown prices for sub activities, as appropriate. The total of the prices of the items in the Schedule of Priced Activities is the Proposer’s offer to complete the works on a “single responsibility” basis. The cost of any items that the Proposer may have omitted is deemed to be included in the price of other items in the Schedule of Priced Activities and Sub-activities and will not be paid for separately by the Employer. - The prices shall be either fixed or adjustable as specified in the PDS. - In the case of Fixed Price, prices quoted by the Proposer shall be fixed during the Proposer’s performance of the contract and not subject to variation on any account. A Proposal submitted with an adjustable price quotation will be treated as non-responsive and rejected. - In the case of Adjustable Price, prices quoted by the Proposer shall be subject to adjustment during performance of the contract to reflect changes in the cost elements in accordance with the procedures specified in the corresponding Appendix to the Contract Agreement. A Proposal submitted with a fixed price quotation will not be rejected, but the price adjustment will be treated as zero. Proposers are required to indicate the source of labor and material indices in the corresponding Form in Section IV, Proposal Forms. - If so indicated in ITP 1.1, Proposals are being invited for individual lots (contracts) or for any combination of lots (packages). Proposers wishing to offer any price reduction (discount) for the award of more than one Contract shall specify in their Letter of Proposal the price reductions applicable to each package, or alternatively, to individual Contracts within the package, and the manner in which the price reductions will apply. However, discounts on the condition of award of more that one contract will not be considered for Proposal evaluation purpose. - Proposers wishing to offer any unconditional discount shall specify in their Letter of Proposal the offered discounts and the manner in which price discounts will apply. - All duties, taxes, and other levies payable by the Contractor under the Contract, or for any other cause, as of the date 28 days prior to the deadline for submission of Proposals, shall be included in the Proposal price submitted by the Proposer. |
| - Proposal Currencies | - The currency (ies) of the Proposal and the currency (ies) of payments shall be the same and shall be as specified in the PDS. - Proposers may be required by the Employer to justify, to the Employer’s satisfaction, their local and foreign currency requirements, and to substantiate that the amounts included in the Schedule of Priced Activities and Sub-activities and shown in the Schedule of Adjustment Data in the Appendix to the Proposal are reasonable, in which case a detailed breakdown of the foreign currency requirements shall be provided by Proposers. |
| - Documents Establishing the Qualification of the Proposer | - In accordance with Section III, Evaluation and Qualification Criteria, to establish that the Proposer continues to meet the qualification criteria used, the Proposer shall provide updated information on any assessed aspect that changed from that time. - If a margin of preference applies as specified in accordance with ITP 39.1, domestic Proposers, individually or in joint ventures, applying for eligibility for domestic preference shall supply all information required to satisfy the criteria for eligibility specified in accordance with ITP 39.1. - Any change in the structure or formation of a Proposer (including, in the case of a JV, any change in the structure or formation of any member and also including any change in any Specialized Subcontractor) shall be subject to the written approval of the Employer prior to the deadline for submission of Proposals. Such approval shall be denied if (i) a Proposer proposes to associate with a disqualified Proposer or in case of a disqualified joint venture, any of its members; (ii) as a consequence of the change, the Proposer no longer substantially meets the qualification criteria set forth in the Section 3 or (iii) in the opinion of the Employer, the change may result in a substantial reduction in competition. Any such change should be submitted to the Employer not later than fourteen (14) days after the Notice of Request for Proposals. |
| - Documents Establishing Conformity of the Works | - Pursuant to ITP 12.2 (f), the Proposer shall furnish, as part of its Proposal documents establishing the conformity to the RFP Documents of the Works that the Proposer proposes to design and build under the Contract. - The documentary evidence of the conformity of the Works and Operation Service with the RFP documents may be in the form of literature, drawings and data, and shall include: - the documents specified in Section IV (Proposal Forms)- Technical Proposal; - detailed description of the essential technical and functional / performance characteristics of the proposed Works, in response to the Employer’s Requirements; and - adequate evidence demonstrating the substantial responsiveness of the Works and the Operation Service to the Employer’s Requirements. Proposers shall note that standards for workmanship, materials and equipment designated by the Employer in the RFP Document are intended to be descriptive (establishing standards of quality and performance) only and not restrictive. The Proposer may substitute alternative standards, in its technical Proposal, provided it demonstrates to the Employer’s satisfaction that the substitutions are substantially equivalent or superior to the standards designated in the Performance / Functional requirements specified by the Employer. - The Proposer shall be responsible for ensuring that any proposed subcontractor complies with the requirements of ITP 4, and that any Works to be provided by the subcontractor comply with the requirements of ITP 5 and ITP 18.1. |
| - Securing the Proposal | - The Proposer shall furnish as part of its Proposal, either a Proposal-Securing Declaration or a Proposal Security as specified in the PDS, in original form and, in the case of a Proposal Security, in the amount and currency specified in the PDS. - A Proposal-Securing Declaration shall use the form included in Section IV, Proposal Forms. - If a Proposal Security is specified pursuant to ITP 19.1, the Proposal security shall be a demand guarantee in any of the following forms at the Proposer’s option: - an unconditional guarantee issued by a bank or a non-bank financial institution (such as an insurance, bonding or surety company); - an irrevocable letter of credit; - a cashier’s or certified check; or - another security indicated in the PDS, from a reputable source from an eligible country. If an unconditional guarantee is issued by a non-bank financial institution located outside the Employer’s Country the issuing non-bank financial institution shall have a correspondent financial institution located in the Employer’s Country to make it enforceable unless the Employer has agreed in writing, prior to Proposal submission, that a correspondent financial institution is not required. - In the case of a bank guarantee, the Proposal Security shall be submitted either using the Proposal Security Form included in Section IV, Proposal Forms or in another substantially similar format approved by the Employer prior to Proposal submission. In either case, the form must include the complete name of the Proposer. The Proposal Security shall be valid for twenty-eight days (28) beyond the original date of expiry of the Proposal validity, or beyond any extended date if requested under ITP 20.2. - If a Proposal Security or a Proposal-Securing Declaration is specified pursuant to ITP 19.1, any Proposal not accompanied by a substantially responsive Proposal Security or Proposal-Securing Declaration shall be rejected by the Employer as non-responsive. - If a Proposal Security is specified in accordance with ITP 19.1, the Proposal Security of the Proposers shall be returned as promptly as possible once the successful Proposer has signed the Contract, furnished the required Performance Security, and if required in the PDS, the Environmental and Social (ES) Performance Security. - The Proposal Security may be forfeited: - if a Proposer withdraws its Proposal prior to the expiry date of the Proposal validity specified by the Proposer on the Letter of Proposal or any extended date provided by the Proposer; or - if the successful Proposer fails to: - sign the Contract in accordance with ITP 53; or - furnish a Performance Security and if required in the PDS, the Environmentaland Social (ESHS) Performance Security, in accordance with ITP 54. - The Proposal Security or the Proposal-Securing Declaration of a JV shall be in the name of the JV that submits the Proposal. If the JV has not been legally constituted into a legally enforceable JV at the time of submission of Proposals, the Proposal Security or the Proposal-Securing Declaration shall be in the names of all future members as named in the letter of intent referred to in ITP 4.1. - If a Proposal Security is not required in the PDS, and: - if a Proposer withdraws its Proposal prior to the expiry date of the Proposal validity specified by the Proposer on the Letter of Proposal or any extended date provided by the Proposer; or - if the successful Proposer fails to: - sign the Contract in accordance with ITP 53; or - furnish a performance security and if required in the PDS, the Environmental and Social(ES) Performance Security, in accordance with ITP 54, - the Employer may, if provided for in the PDS, declare the Proposer disqualified to be awarded a contract by the Employer for a period of time as stated in the PDS. |
| - Period of Validity of Proposals | - Proposals shall remain valid until the date specified in the PDS or any extended date if amended by the Employer in accordance with ITP 8. A Proposal that is not valid until the date specified in the PDS, or any extended date if amended by the Employer in accordance with ITP 8, shall be rejected by the Employer as nonresponsive. - In exceptional circumstances, prior to the date of expiry of the Proposal validity, the Employer may request the Proposers to extend the date of of validity until a specified date. The request and the responses to the request shall be made in writing. A Proposer may refuse the request without risking execution of the Proposal-Securing Declaration or forfeiting the Proposal Security. Except as provided in ITP 20.3, a Proposer agreeing to the request will not be required or permitted to modify its Proposal, but will be required to ensure that the Proposal Security is extended for a correspondingly longer period, pursuant to ITP 19.4. - In the case of fixed price contracts, if the award is delayed by a period exceeding fifty-six (56) days beyond the date of expiry of the Proposal validity specified in accordance with ITP 20.1, the contract price will be adjusted as specified in the PDS. Proposal evaluation will be based on the Proposal prices without taking into consideration the above correction. |
| - Format and Signing of Proposal | - The original and all copies of the Proposal, each consisting of the documents listed in ITP 12, shall be typed or written in indelible ink and shall be signed by a person or persons duly authorized to sign on behalf of the Proposer. The authorization must be in writing as specified in the PDS, and included in the Proposal pursuant to ITP 12.2(d). The name and position held by each person signing the authorization must be typed or printed below the signature. All pages of the Proposal where entries or amendments have been made shall be signed or initialed by the person signing the Proposal. - In case the Proposer is a JV, the Proposal shall be signed by an authorized representative of the JV on behalf of the JV, and so as to be legally binding on all the members as evidenced by a power of attorney signed by their legally authorized representatives. - The Proposal shall contain no interlineations, erasures, or overwriting, except to correct errors made by the Proposer, in which case such corrections shall be initialed by the person or persons signing the Proposal. - The Proposer shall furnish in the Proposal Submission Form (Section IV) information regarding commissions or gratuities, if any, paid or to be paid to agents relating to this procurement and to the execution of the Contract should the Proposer be successful. |

D. Submission of Proposals

| - Submission, Sealing and Marking of Proposals | - Unless the PDS states that Proposals are to be submitted electronically the following procedures shall apply. - The Proposer shall deliver the Proposal in two separate, sealed envelopes. One envelope containing the Technical Part and the other the Financial Part. These two envelopes shall be enclosed in a sealed outer envelope and clearly marked “Proposal - Original”. - In addition, the Proposer shall prepare copies of the Proposal, in the number specified in the PDS. Copies of the Technical Part shall be placed in a separate sealed envelope marked “Copies: Technical Part”. Copies of the Financial Part shall be placed in a separate sealed envelope marked “Copies: Financial Part”. The Proposer shall place both of these envelopes in a separate, sealed outer envelope marked “Proposal - Copies”. In the event of any discrepancy between the original and the copies, the original shall prevail. - If alternative Proposals are permitted in accordance with ITP 14, the alternative Proposals shall be submitted as follows: the original of the alternative Proposal Technical Part shall be placed in a sealed envelope marked “Alternative Proposal – Technical Part” and the Financial Part shall be placed in a sealed envelope marked “Alternative Proposal – Financial Part” and these two separate sealed envelopes then enclosed within a sealed outer envelope marked “Alternative Proposal – Original”, the copies of the alternative Proposal will be placed in separate sealed envelopes marked “Alternative Proposal – Copies Of Technical Part”, and “Alternative Proposal – Copies Of Financial Part” and enclosed in a separate sealed outer envelope marked “Alternative Proposal - Copies” - The inner and outer envelopes shall: - bear the name and address of the Proposer; - be addressed to the Employer, at the address given in the PDS for ITP 23.1; and - bear the Contract(s) name, the Invitation for Proposals (RFP) title and number, as specified in the PDS for ITP 1.1, and the statement “Do Not Open Before [time and date],” to be completed with the time and date specified in the PDS for ITP 23.1. - If the outer envelope is not sealed and marked as required by ITP 22.1 and ITP 22.2, the Employer will assume no responsibility for the Proposal’s misplacement or premature opening. |
| --- | --- |
| - Deadline for Submission of Proposals | - Proposals must be received by the Employer at the address specified no later than the date and time specified, in the PDS. Proposers have the option of submitting their Proposals electronically if specified in the PDS. - The Employer may, at its discretion, extend the deadline for submission of Proposals by amending the RFP Documents in accordance with ITP 8.3, in which case all rights and obligations of the Employer and Proposers will thereafter be subject to the deadline as extended. |
| - Late Proposals | - The Employer shall not consider any Proposal that arrives after the deadline for submission of Proposals, in accordance with ITP 23. Any Proposal received by the Employer after the deadline for submission of Proposals shall be declared late, rejected, and returned unopened to the Proposer. |
| - Withdrawal, Substitution, and Modification of Proposals | - A Proposer may withdraw, substitute, or modify its Proposal after it has been submitted, and before the deadline for submission of Proposals, by sending a written notice, duly signed by an authorized representative, including a copy of the authorization in accordance with ITP 21.1, (except that withdrawal notices do not require copies). The corresponding substitution or modification of the Proposal must accompany the respective written notice. All notices must be: - prepared and submitted in accordance with ITP 21 and ITP 22 (except that withdrawals notices do not require copies), and in addition, the respective envelopes shall be clearly marked “Withdrawal,” “Substitution, (“Technical Part” and/or “Financial Part”)” “Modification (“Technical Part” and/or “Financial Part”);” and - received by the Employer prior to the deadline prescribed for submission of Proposals, in accordance with ITP 23. |

E. Opening of Technical Parts of Proposals

| - Opening of Technical Part by Employer | - Except as in the cases specified in ITP 24 and ITP 25, the Employer shall conduct the Technical Part opening in public, in the presence of Proposers` designated representatives and anyone who chooses to attend at the address, date and time specified in the PDS. Any specific electronic Proposal opening procedures, if permitted, shall be as specified in the PDS. - First, the written notice of withdrawal in the envelopes marked “Withdrawal” shall be opened and read out and the envelope with the corresponding Proposal shall not be opened, but returned to the Proposer. No Proposal withdrawal shall be permitted unless the corresponding withdrawal notice contains a valid authorization to request the withdrawal and is read out at Proposal opening. - Next, envelopes marked “Substitution” shall be opened and read out and exchanged with the corresponding Technical Part being substituted, and the substituted Proposal shall not be opened, but returned to the Proposer. No Proposal substitution shall be permitted unless the corresponding substitution notice contains a valid authorization to request the substitution and is read out at Proposal opening. - Next, envelopes marked “Modification” shall be opened and read out with the corresponding Proposal. No Proposal modification shall be permitted unless the corresponding modification notice contains a valid authorization to request the modification and is read out at Proposal opening. - Next, all other envelopes marked “Technical Part” shall be opened one at a time. All envelopes marked “Financial Part” shall remain sealed and kept by the Employer in safe custody until they are opened, at a later public opening, following the evaluation of the Technical Part of the Proposals. On opening the Technical Part envelopes, the Employer shall read out: the name of the Proposer and whether there is a modification; the presence or absence of a Proposal security or a Proposal-Securing Declaration; and other details as the Employer, at its discretion, may consider appropriate. - Only Technical Parts of Proposals and Alternative Proposal - Technical Parts that are opened and read out at Proposal opening shall be considered further. At the Proposal opening the Employer shall neither discuss the merits of any Proposal nor reject any Proposal (except for late Proposals, in accordance with ITP 24.1). - The Employer shall prepare a record of the Technical Parts of public opening that shall include, as a minimum: the name of the Proposer and whether there is a withdrawal, substitution, or modification. The Proposers’ representatives who are present shall be requested to sign the record. The omission of a Proposer’s signature on the record shall not invalidate the contents and effect of the record. A copy of the record shall be distributed to all Proposers who submitted Proposals in time, and posted online when electronic procurement is permitted. |
| --- | --- |

F. Evaluation of Proposals – General Provisions

| - Confidentiality | - Information relating to the evaluation of the Technical Part shall not be disclosed to Proposers or any other persons not officially concerned with the RFP process until the notification of evaluation of the Technical Part in accordance with ITP 33. - Information relating to the evaluation of the Financial Part and recommendation of contract award, shall not be disclosed to Proposers or any other persons not officially concerned with the RFP process until the Notification of Intention to Award the Contract is transmitted to all Proposers in accordance with ITP 49. - Any effort by a Proposer to influence the Employer in the evaluation of the Proposals may result in the rejection of its Proposal. - Notwithstanding ITP 27.1 and ITP 27.2, from the time of Proposal opening to the time of Contract award, if any Proposer wishes to contact the Employer on any matter related to the RFP process, it should do so in writing. |
| --- | --- |
| - Clarification of Proposals | - To assist in the examination, evaluation, and comparison of the Proposals, and qualification of the Proposers, the Employer may, at its discretion, ask any Proposer for clarification of its Proposal. Any clarification submitted by a Proposer that is not in response to a request by the Employer shall not be considered. The Employer’s request for clarification and the response shall be in writing. - If a Proposer does not provide clarifications of its Proposal by the date and time set in the Employer’s request for clarification, its Proposal may be rejected. |
| - Deviations, Reservations, and Omissions | During the evaluation of Proposals, the following definitions apply: - “Deviation” is a departure from the requirements specified in the RFP document; - “Reservation” is the setting of limiting conditions or withholding from complete acceptance of the requirements specified in the RFP document; and - “Omission” is the failure to submit part or all the information or documentation required in the RFP document. |

G. Evaluation of Technical Parts of Proposals

| - Determination of Responsiveness of Technical Parts | - The Employer will examine the Technical Parts, including any alternatives submitted by Proposers, to determine whether they are complete, have been properly signed, and are generally in order. - The Employer’s determination of a Technical Part’s substantial responsiveness is to be based on the contents of the Proposal itself. For purposes of this determination, a substantially responsive Proposal is one that materially conforms to the requirements of the RFP Document without material deviation, reservation, or omission. A material deviation, reservation, or omission is one that: - if accepted, would: - affect in any substantial way the scope, quality, or performance of the Works specified in the Contract; or - limit in any substantial way, inconsistent with the RFP Document, the Employer’s rights or the Proposer’s obligations under the proposed Contract; or - if rectified, would unfairly affect the competitive position of other Proposers presenting substantially responsive Proposals. - Provided that a Technical Part is substantially responsive, the Employer may waive any nonmaterial nonconformity in the Proposal. - Provided that a Proposal is substantially responsive, the Employer may request the Proposer to submit the necessary information or documentation, within a reasonable period of time, to rectify nonmaterial nonconformities in the Proposal related to documentation requirements. |
| --- | --- |
| - Evaluation of Technical Parts | - The Employer’s evaluation of technical proposals will be carried out as specified in Section III, Evaluation and Qualification Criteria. - The scores to be given to technical factors and sub factors are specified in the PDS. |
| - Evaluation of Proposer’s Qualification | - The Employer shall determine to its satisfaction that, on the basis of updated documentary evidence submitted in accordance with ITP 12.2 (e), and Section III- Evaluation and Qualification Criteria, the Proposer continues to be qualified to satisfactorily perform the Contract. - Only Proposals that are both substantially responsive to the RFP document and are qualified shall have their envelopes marked “Financial Part” opened at the second public opening. |
| - Notification of evaluation of Technical Parts | - Following the completion of the evaluation of the Technical Parts of Proposals, the Employer shall make the following notifications: - Notify in writing those Proposers whose Proposals were considered substantially non-responsive to the requirements in the RFP, advising them of the following information: - the grounds on which their Technical Part has been considered to be non-responsive; - their envelope marked “Financial Part” will be returned to them unopened after the completion of the Proposal evaluation process and the signing of the Contract; - simultaneously, notify in writing those Proposers whose Proposals were considered substantially responsive to the requirements in the RFP, advising them that their Proposal has been evaluated as substantially responsive to the RFP; and - notify all Proposers in accordance with the one of following two options: - Option 1: when Best and Final Offer (BAFO) or Negotiations is not to be applied, the date, time and location of the public opening of the envelopes marked ‘Financial Part”, or; - Option 2: when BAFO or Negotiations apply as specified in the PDS ITP 44 and ITP 46 respectively, that: (i) the envelopes marked ‘Financial Part’ will not be opened in public, but in the presence of a Probity Assurance Provider (Probity Auditor) appointed by the Employer, and that (ii) the announcement of the names of the Proposers whose Financial Parts will be opened and the total Proposal prices will be deferred to the time that the Notification of Intention to Award the contract is issued. |

H. Opening of Financial Parts

| - Public Opening of Financial Parts when BAFO or negotiations do not apply | - When BAFO or negotiations do not apply as specified in the PDS, the Financial Parts will be opened in public by the Employer in the presence of Proposers, or their designated representatives, and anyone else who chooses to attend. Each envelope marked “Financial Part” shall be inspected to confirm that it has remained sealed and unopened. These envelopes shall then be opened by the Employer. The Employer shall read out the names of each Proposer, the technical score, the total Proposal prices, per lot (contract) if applicable, including any discounts, the presence or absence of a Proposal Security or Proposal-Securing Declaration, if required and any other details as the Employer may consider appropriate. Only discounts read out at the public opening shall be considered for evaluation. The Letter of Proposal - Financial Part and the Schedule of Rates and Prices (if any) are to be initialed by representatives of the Employer attending the public opening in the manner specified in the PDS. - The Employer shall prepare a record of the Financial Part of the Proposal opening that shall include, as a minimum: - the name of the Proposers whose Financial Part was opened; - the Proposal prices, per lot (contract) if applicable, including any discounts. - The Proposers whose envelopes marked “Financial Part” have been opened, or their representatives who are present, shall be requested to sign the record. The omission of a Proposer’s signature on the record shall not invalidate the contents and effect of the record. A copy of the record shall be distributed to all Proposers. |
| --- | --- |
| - Opening of Financial Parts when BAFO or negotiations apply | - When, as specified in the PDS, BAFO or negotiations apply the Financial Parts will not be opened in public, and will be opened in the presence of a Probity Assurance Provider appointed by the Employer. - At the opening each of the envelopes marked “Financial Part” shall be inspected to confirm that they have remained sealed and unopened. These envelopes shall then be opened by the Employer. The Employer shall record the names of each Proposer, and the total Proposal prices and any other details as the Employer may consider appropriate. The Letter of Proposal - Financial Part and the Schedule of Rates and Prices (if any) are to be initialed by representatives of the Employer attending the public opening and by the Probity Assurance Provider. - The Employer shall prepare a record of the opening of the Financial Part envelopes that shall include, as a minimum: - the name of the Proposers whose Financial Part was opened; - the Proposal prices including any discounts; and - the Probity Assurance Provider’s report of the opening of the Financial Part. - The Probity Assurance Provider shall sign the record. The contents of the envelopes marked ‘Financial Part’ and the record of the opening shall be kept in safe custody by the Employer and not disclosed to anyone until the time of the transmission of the Notification of Intention to Award the contract. |

I. Evaluation of Financial Part

| - Nonmaterial Nonconformities | - Provided that a Proposal is substantially responsive, the Employer shall rectify quantifiable nonmaterial nonconformities related to the Proposal Price. To this effect, the Proposal Price shall be adjusted, for comparison purposes only, to reflect the price of a missing or non-conforming item or component by adding the average price of the item or component quoted by substantially responsive Proposers. If the price of the item or component cannot be derived from the price of other substantially responsive Proposers, the Employer shall use its best estimate. |
| --- | --- |
| - Arithmetic Correction | - The Employer shall correct arithmetical errors on the following basis: - Priced Sub-activity Schedule: where there are errors between the total of the amounts given under the column for Sub-activity Price and the amount given under the total for the Sub-activity, the former shall prevail and the latter will be corrected accordingly; - Priced Activity Schedule: where there are errors between the total of the amounts given under the column for the Activity Price and the amount given under the total price of Activities, the former shall prevail, and the latter will be corrected accordingly; - where there are errors between the total of the amounts in the Priced Sub-activity Schedule and the corresponding amount in the Priced Activity Schedule, the former shall prevail, and the latter will be corrected accordingly; - Grand Summary: where there are errors between the total price of Activities in the Schedule of Priced Activities and the amount given in Grand Summary, the former shall prevail, and the latter will be corrected accordingly; and - if there is a discrepancy between words and figures, the amount in words shall prevail, unless the amount expressed in words is related to an arithmetic error, in which case the amount in figures shall prevail subject to (a) to (d) above. - A Proposer shall be requested to accept the correction of arithmetical errors. Failure to accept the correction in accordance with ITP 37.1 shall result in the rejection of the Proposal. |
| - Conversion to Single Currency | - For evaluation and comparison purposes, the currency (ies) of the Proposal shall be converted into a single currency as specified in the PDS. |
| - Margin of Preference | - Unless otherwise specified in the PDS, a margin of preference for domestic Proposers shall not apply. |
| - Evaluation Process Financial Parts | - To evaluate each Proposal’s Financial Part, the Employer shall consider the following: - the Proposal price, excluding provisional sums and the provision, if any, for contingencies in the Schedule of Rates and Prices (if any); - price adjustment for correction of arithmetic errors in accordance with ITP 37.1; - price adjustment due to discounts offered in accordance with ITP 15.7; - price adjustment due to quantifiable nonmaterial nonconformities in accordance with ITP 36.1; - converting the amount resulting from applying (a) to (c) above, if relevant, to a single currency in accordance with ITP 38.1; and - any additional evaluation factors indicated in the PDS and detailed in Section III, Evaluation and Qualification Criteria. - If price adjustment is allowed in accordance with ITP 15.5, the estimated effect of the price adjustment provisions of the Conditions of Contract, applied over the period of execution of the Contract, shall not be taken into account in Proposal evaluation. - If this RFP allows Proposers to quote separate prices for different lots (contracts), each lot will be evaluated separately to determine the Most Advantageous Proposal using the methodology specified in Section III, Evaluation and Qualification Criteria. Discounts that are conditional on the award of more than one lot, or slice shall not be considered for Proposal evaluation. |
| - Abnormally Low Proposals | - An Abnormally Low Proposal is one where the Proposal price, in combination with other elements of the Proposal, appears so low that it raises material concerns as to the capability of the Proposer to perform the Contract for the offered Proposal Price. - In the event of identification of a potentially Abnormally Low Proposal, the Employer shall seek written clarifications from the Proposer, including detailed price analyses of its Proposal price in relation to the subject matter of the contract, scope, proposed methodology, schedule, allocation of risks and responsibilities and any other requirements of the RFP Document. - After evaluation of the price analyses, in the event that the Employer determines that the Proposer has failed to demonstrate its capability to perform the Contract for the offered Proposal Price, the Employer shall reject the Proposal. |
| - Unbalanced or Front Loaded Proposals | - If the Proposal that is evaluated as the lowest evaluated cost is, in the Employer’s opinion, seriously unbalanced or front loaded the Employer may require the Proposer to provide written clarifications. Clarifications may include detailed price analyses to demonstrate the consistency of the Proposal prices with the scope of the Works, proposed methodology, schedule and any other requirements of the RFP Document. - After the evaluation of the information and detailed price analyses presented by the Proposer, the Employer may: - accept the Proposal, or - if appropriate, require that the total amount of the Performance Security be increased, at the expense of the Proposer, to a level not exceeding twenty percent (20%) of the Contract Price; or - reject the Proposal. |

J. Evaluation of Combined Technical and Financial Part

| - Evaluation of Combined Technical and Financial Parts | - The Employer’s evaluation of responsive Proposals will take into account technical factors, in addition to cost factors in accordance with Section III Evaluation and Qualification Criteria. The weight to be assigned for the Technical factors and cost is specified in the PDS. The Employer will rank the proposals based on the evaluated Proposal score (B). |
| --- | --- |
| - Best and Final Offer (BAFO) | - After completion of the combined technical and financial evaluation of proposals, if specified in the PDS, the Employer may invite those Proposers to submit their BAFOs. The procedure for submitting BAFOs will be specified in the PDS. BAFO is a final opportunity for Proposers to improve their Proposals without changing the specified business function and performance requirements in accordance with the RFP Documents. Proposers are not obliged to submit a BAFO. Where BAFO is used there will be no negotiation after BAFO. - BAFO will apply a two envelope procurement process. The submission of BAFOs, opening of the Technical Parts and Financial Parts and the evaluation of Proposals will follow the procedures described for the Technical, Financial and Combined evaluation above, as appropriate. |
| - Most Advantageous Proposal (MAP) | - The Most Advantageous Proposal is the Proposal of the Proposer that meets the Qualification Criteria, and whose Proposal has been determined to be: - substantially responsive to the RFP; and - the best evaluated Proposal i.e. the highest scoring Proposal, in the combined technical and financial evaluation. |
| - Negotiations | - If specified in the PDS, the Employer may conduct negotiations following the evaluation of Proposals and before the final contract award. The procedure of the negotiations will be specified in the PDS. - Negotiations shall be held in the presence of Probity Assurance Provider appointed by the Employer. - Negotiations may address any aspect of the contract so long as they do not change the specified business function and performance requirements. - The Employer may negotiate first with the Proposer that has the Most Advantageous Proposal. If the negotiations are unsuccessful the Employer may negotiate with the Proposer that has the next best Most Advantageous Proposal, and so on down the list until a successful negotiated outcome is achieved. |
| - Employer’s Right to Accept Any Proposal, and to Reject Any or All Proposals | - The Employer reserves the right to accept or reject any Proposal, and to annul the RFP process and reject all Proposals at any time prior to contract award, without thereby incurring any liability to Proposers. In case of annulment, all Proposals submitted and specifically, Proposal securities shall be promptly returned to the Proposers. |
| - Standstill Period | - The Contract shall not be awarded earlier than the expiry of the Standstill Period. The Standstill Period shall be ten (10) Business Days unless extended in accordance with ITP 52. The Standstill Period commences the day after the date the Employer has transmitted to each Proposer (that has not already been notified that it has been unsuccessful) the Notification of Intention to Award the Contract. Where only one Proposal is submitted, or if this contract is in response to an emergency situation recognized by the Bank, the Standstill Period shall not apply. |
| - Notification of Intention to Award | - The Employer shall send to each Proposer (that has not already been notified that it has been unsuccessful) the Notification of Intention to Award the Contract to the successful Proposer. The Notification of Intention to Award shall contain, at a minimum, the following information: - the name and address of the Proposer submitting the successful Proposal; - the Contract price of the successful Proposal; - the total combined score of the successful Proposal; - the names of all Proposers who submitted Proposals, and their Proposal prices as readout and as evaluated prices and technical score; - a statement of the reason(s) the Proposal (of the unsuccessful Proposer to whom the notification is addressed) was unsuccessful; - the expiry date of the Standstill Period; and - instructions on how to request a debriefing or submit a complaint during the standstill period; |

K. Award of Contract

| - Award Criteria | - Subject to ITP 47.1, the Employer shall award the Contract to the Proposer with the Most Advantageous Proposal, provided that the Proposer is determined to be eligible and qualified to perform the Contract satisfactorily. |
| --- | --- |
| - Notification of Award | - Prior to the date of expiry of the Proposal validity, and upon expiry of the Standstill Period, specified in ITP 48.1 or any extension thereof, and upon satisfactorily addressing any complaint that has been filed within the Standstill Period, the Employer shall notify the successful Proposer, in writing, that its Proposal has been accepted. The notification of award (hereinafter and in the Conditions of Contract and Contract Forms called the “Letter of Acceptance”) shall specify the sum that the Employer will pay the Contractor in consideration of the execution of the Contract (hereinafter and in the Conditions of Contract and Contract Forms called “the Contract Price”). - Within ten (10) Business days from the transmission of the Letter of Acceptance, the Employer shall publish the Contract Award Notice which shall contain, at a minimum, the following information: - name and address of the Employer; - name and reference number of the contract being awarded, and the selection method used; - names of all Proposers that submitted Proposals, and their Proposal prices as read out at Proposal opening, and as evaluated; - name of Proposers whose Proposals were rejected and the reasons for their rejection; - the name of the successful Proposer, the final total contract price, the contract duration and a summary of its scope; and - successful Proposer’s Beneficial Ownership Disclosure Form, if specified in PDS ITP 53.1. - The Contract Award Notice shall be published on the Employer’s website with free access if available, or in at least one newspaper of national circulation in the Employer’s Country, or in the official gazette. The Employer shall also publish the contract award notice in UNDB online. - Until a formal contract is prepared and executed, the Letter of Acceptance shall constitute a binding Contract. |
| - Debriefing by the Employer | - On receipt of the Borrower’s Notification of Intention to Award referred to in ITP 49, an unsuccessful Proposer has three (3) Business Days to make a written request to the Employer for a debriefing. The Employer shall provide a debriefing to all unsuccessful Proposers whose request is received within this deadline. - Where a request for debriefing is received within the deadline, the Employer shall provide a debriefing within five (5) Business Days, unless the Employer decides, for justifiable reasons, to provide the debriefing outside this timeframe. In that case, the standstill period shall automatically be extended until five (5) Business Days after such debriefing is provided. If more than one debriefing is so delayed, the standstill period shall not end earlier than five (5) Business Days after the last debriefing takes place. The Employer shall promptly inform, by the quickest means available, all Proposers of the extended standstill period. - Where a request for debriefing is received by the Employer later than the three (3)-Business Day deadline, the Employer should provide the debriefing as soon as practicable, and normally no later than fifteen (15) Business Days from the date of publication of Public Notice of Award of contract. Requests for debriefing received outside the three (3)-day deadline shall not lead to extension of the standstill period. - Debriefings of unsuccessful Proposers may be done in writing or verbally. The Proposers shall bear their own costs of attending such a debriefing meeting. |
| - Signing of Contract | - The Employer shall send to the successful Proposer the Letter of Acceptance including the Contract Agreement, and, if specified in the PDS, a request to submit the Beneficial Ownership Disclosure Form providing additional information on its beneficial ownership. The Beneficial Ownership Disclosure Form, if so requested, shall be submitted within eight (8) Business Days of receiving this request. - The successful Proposer shall sign, date and return to the Employer, the Contract Agreement within twenty-eight (28) days of its receipt. |
| - Performance Security | - Within twenty-eight (28) days of the receipt of the Letter of Acceptance from the Employer, the successful Proposer shall furnish the Performance Security and if required in the PDS, the Environmental and Social (ES) Performance Security, in accordance with the General Conditions, subject to ITP 42.2 (b), using the Performance Security and ES Performance Security Forms included in Section X, Contract Forms, or another form acceptable to the Employer. If the performance security furnished by the successful Proposer is in the form of a bond, it shall be issued by a bonding or insurance company that has been determined by the successful Proposer to be acceptable to the Employer. A foreign institution providing a bond shall have a correspondent financial institution located in the Employer’s Country, unless the Employer has agreed in writing that a correspondent financial institution is not required. - Failure of the successful Proposer to submit the above-mentioned Performance Security and if required in the PDS, the Environmental and Social (ES) Performance Security, or sign the Contract shall constitute sufficient grounds for the annulment of the award and forfeiture of the Proposal security. In that event the Employer may award the Contract to the next lowest evaluated Proposer whose offer is substantially responsive and is determined by the Employer to be qualified to perform the Contract satisfactorily. |
| - Procurement Related Complaint | - The procedures for making a Procurement-related Complaint are as specified in the PDS. |

Section II – Proposal Data Sheet (PDS)

The following specific data for the proposed Works shall complement, supplement, or amend the provisions in the Instructions to Proposers (ITP). Whenever there is a conflict, the provisions herein shall prevail over those in ITP.

[Instructions for completing the Proposal Data Sheet are provided, as needed, in the notes in italics mentioned for the relevant ITP]

| ITP Reference | A. General |  |
| --- | --- | --- |
| ITP 1.1 | The reference number of the Request for Proposals is: MV-MONPI-223416-CW-RFP The Employer is: Ministry of National Planning, Housing and Infrastructure The name of the RFP is: Design, Build and Operation of 10MLD Sewage Treatment Plant in Hulhumalé Phase 1 Project Number: TES/2021/W-107 |
| ITP 2.1 | The Borrower is: Republic of Maldives |
| ITP 2.1 | Loan or Financing Agreement amount: USD 16.5 Million The name of the Project is: Maldives Urban Development and Reslilience Project |
| ITP 1.3 (a) | Not Applicable |
| ITP 3.2 | Delete the words “initial selection process and prequalification process” |
| ITP 4.1 | Maximum number of members in the JV shall be: Three (3) |
| ITP 4.1 | The Winning proposer must register the entitiy in the Republic of Maldives as per the Law |
| ITP 4.5 | A list of debarred firms and individuals is available on the Bank’s external website: http://www.worldbank.org/debarr. Delete “be initially selected for, prequalified for, Proposal for,” |
| B. RFP Document |  |
| ITP 7.1 | For Clarification of Proposal purposes only, the Employer’s address is: # Attention: # Ms. Fathimath Rishfa Ahmed # Chief Procurement Executive, # National Tender Address: Ministry of Finance City: Male’ ZIP Code: 20379 Country: Republic of Maldives Telephone: (+960) 3349102, (+960) 3349106, (+960) 3349147 Electronic mail address: ibrahim.aflah@finance.gov.mv CC: tender@finance.gov.mv Requests for clarification should be received by the Employer no later than: 1330 hours Maldives Time on August 27, 2021. |
| ITP 7.1 | Web page: www.finance.gov.mv/tenders |
| ITP 7.4 | A Pre-Proposal meeting will take place at the following date, time: Date:12th August 2021 Time:1300 hrs All the registered Bidders as well as the Bidders who submit by email their interest to attend the meeting will receive an official email from National Tender with the link to join the Online Video Conference Meeting 2 calendar days before the meeting. Only 1 representative from each Bidder shall join the meeting. The Employer shall not be responsible for any interruptions or disconnections during the Online Video Conference Meeting. # A site visit conducted by the Employer shall be organized. |
| C. Preparation of Proposals |  |
| ITP 11.1 | The language of the Proposal is: English All correspondence exchange shall be in English language. |
| ITP 12.2 (k) | The Proposer shall submit with its Proposal the following additional documents: The list of additional documents shall include the following: # Code of Conduct for Contractor’s Personnel (ES) The Proposer shall submit its Code of Conduct that will apply to Contractor’s Personnel (as defined in Sub-Clause 1.1.16 of the General Conditions), to ensure compliance with the Contractor’s Environmental and Social (ES) obligations under the Contract. The Proposer shall use for this purpose the Code of Conduct form provided in Section IV. No substantial modifications shall be made to this form, except that the Proposer may introduce additional requirements, including as necessary to take into account specific Contract issues/risks. [Note: Complete and include the risks to be addressed by the Code in accordance with works’ requirements, e.g. risks associated with: labor influx, spread of communicable diseases, sexual harassment, gender-based violence, illicit behavior and crime, and maintaining a safe environment etc.] In addition, the Bidder shall detail how this Code of Conduct will be implemented. This will include: how it will be introduced into conditions of employment/engagement, what training will be provided, how it will be monitored and how the Operator proposes to deal with any breaches. In addition, the Operator shall be required to submit for approval, and subsequently implement, the Operator’s Environment and Social Management Plan (O-ESMP) and management strategies and implementation plan to manage ESHS risks, in accordance with Appendix 1 to Employers requirement (Design Build Services), that includes the agreed Management Strategies and Implementation Plans described here. |
| 12.2 (e) | Modified to read as “documentary evidence (Section 3 – Qualification Criteria) that the Proposer is eligible and qualified to perform the contract if its Proposal is accepted |
| ITP 14.1 | Alternative Proposals shall not be considered |
| ITP 15.1 | “Proposers shall propose for the following component of the Works on a single responsibility basis:Design, Build and Operation of the sewage treatment facility |
| ITP 15.3 | The prices quoted by the Proposer shall be subject to adjustment during the performance of the Contract. |
| ITP 16.1 | The currency(ies) of the Proposal and the payment currency(ies) shall be in accordance with Alternative B as described below: Alternative B (Proposers allowed to quote in local and foreign currencies): (a) The prices shall be quoted by the Proposer in the Schedules of Priced Activities and Sub-activities separately in the following currencies: - for those inputs to the Works that the Proposer expects to supply from within the Employer’s country, in Maldivian Rufiyya, and further referred to as “the local currency”; and - for those inputs to the Works that the Proposer expects to supply from outside the Employer’s country (referred to as “the foreign currency requirements”), in United States Dollars (USD). |
| ITP 19 | A Proposal Security shall be required and all Proposals must be accompanied by Proposal Security in the form of an unconditional Bank Guarantee of MVR 2,313,000.00 or USD 150,000.00 or an equivalent amount in a convertible currency for the project A Proposal-Securing Declaration shall not be required. |
| ITP 19.3 (d) | Other types of acceptable securities: None |
| ITP 20.1 | The Proposal shall be valid until 180 days (6 months) from the date of Proposal Submission |
| ITP 20.3 | # The Proposal price shall be adjusted by the following factor(s): Not Applicable |
| ITP 21.1 | The written confirmation of authorization to sign on behalf of the Bidder shall consist of: An organizational board resolution or its equivalent, or power of attorney specifying the representative's authority to sign the Proposal on behalf of, and to legally bind, the Bidder. If the Bidder is an intended or an existing Joint Venture, the power of attorney should be signed by all partners and specify the authority of the named representative of the Joint Venture to sign on behalf of, and legally bind, the intended or existing Joint Venture partner. If the Joint Venture has not been formed, include evidence from all proposed Joint Venture partner of their intent to enter into a Joint Venture in the event of a contract award following ITP 4.1 |
| D. Submission of Proposals |  |
| ITP 22.1(b) | In addition to the original of the Proposal, the number of copies is: 2 (Two) (One Hard Copy and (1) digital copy on a USB or Optical Disk. The type of optical disk that should be used is DVD-R or CD-R) |
| ITP 23.1 | For Proposal submission purposes only, the Employer’s address is: # For the attention: Ms. Fathimath Rishfa Ahmed Title/position: Chief Procurement Executive Address: National Tender, Ministry of Finance Ameenee Magu, Malé, Block 379, Postal Code 20379, Republic of Maldives Email address: ibrahim.aflah@finance.gov.mv CC: tender@finance.gov.mv The deadline for Proposal submission is: Date: 16th September 2021 Time: 1400 hrs on Maldivian Time |
| ITP 23.1 | Proposers shall not have the option of submitting their Proposals electronically. |
| E. Opening of TECHNICAL PARTS of PROPOSALS |  |
| ITP 26.1 | The Proposal opening shall take place at: National Tender, Ministry of Finance Ameenee Magu, Malé, Block 379, Postal Code 20379, Republic of Maldives , Date: 16th September 2021 Time: 1400 hrs on Maldivian Time |
| G. Evaluation of Technical Parts of Proposals |  |
| ITP 31. | Technical evaluation will be conducted on a pass/fail basis based on the Criteria stated in Section III – Evaluation and Qualification Criteria. |
| H. Opening of Financial Parts |  |
| ITP 32.1 | Delete the words “Updated” |
| ITP 34.1 | The Letter of Proposal and Price Schedules shall be initialed by one representatives of the Employer conducting Proposal opening. |
| I. Evaluation of Financial Part |  |
| ITP 38.1 | The currency that shall be used for Proposal evaluation and comparison purposes to convert at the selling exchange rate all Proposal prices expressed in various currencies into a single currency is: United States Dollar (USD) The source of exchange rate shall be: Maldives Monitory Authority (MMA) The date for the exchange rate shall be the deadline for submission of Proposals as specified in ITP 23, unless otherwise specified by the Employer. The currency(ies) of the Proposal shall be converted into a single currency in accordance with the procedure under Alternative B that follows: Alternative B: Proposers quote in local and foreign currencies The Employer will convert the amounts in various currencies in which the Proposal Price, corrected pursuant to ITP 37.1, is payable (excluding Provisional Sums) to the single currency identified above at the selling rates established for similar transactions by the authority specified and on the date stipulated above. |
| ITP 39.1 | A margin of domestic preference shall not apply. |
| ITP 40.1 | The Owner shall examine each Bidder’s Financial Section to determine whether such Financial Section is complete and substantially responsive to the Bidding Documents. The Financial Sections, which are substantially responsive to the Bidding Documents, shall be evaluated to determine the lowest evaluated bid. The Owner shall evaluate the Proposal prices by determining and adding various components of cost and prices as under: - Price adjustment for correction of arithmetic errors in accordance with ITP 37.1; plus - Cost of design, development, construction, testing and successful commissioning of STP including the odour control system and sludge management ; plus - NPV of the yearly payments due on account of O & M charges over 10 years of O&M assuming “Indicative Sewage Flow Rate” of 10MLD without considering any price adjustment on account of the adjustment applicable as per ITP 40.1 (f). For the purpose of determining the NPV, discount factor of 9 % per annum shall be applicable. |
| ITP 40.1 (f) | The adjustments shall be determined using the following criteria as detailed in Section III: - Deviation in Time Schedule: No - The Operation Service Proposal prices will be adjusted for Net Present Value in accordance with ITP 43.1 and as specified in Section III; |
| J. Evaluation of Combined Technical and Financial Part |  |
| ITP 43.1 | Not Applicable |
| ITP 44.1 | BAFO does not apply |
| ITP 46.1 | Negotiation does not apply |
| K. Award of Contract |  |
| ITP 53.1 | The successful Proposer is required to submit the Beneficial Ownership Disclosure Form. |
| ITP 54.1 and 54.2 | The successful Proposer shall be required to submit an Environmental and Social (ES) Performance Security. The ES Performance Security will be in the form of a “demand guarantee” in the amount(s) of 3% of the Accepted Contract Amount for the Design Build and in the same currency (ies) of the Accepted Contract Amount. |
| ITP 55.1 | The procedures for making a Procurement-related Complaint are detailed in the “Procurement Regulations for IPF Borrowers (Annex III).” If a Proposer wishes to make a Procurement-related Complaint, the Proposer shall submit its complaint following these procedures, In Writing (by the quickest means available, such as by email), to: For the attention: Ms. Fathimath Rishfa Ahmed Title/position: Procurement Executive Employer: Ministry of Finance Email address: ibrahim.aflah@finance.gov.mv, tender@finance.gov.mv In summary, a Procurement-related Complaint may challenge any of the following: - the terms of this request for proposal document; - the Employer’s decision to exclude a Proposer from the procurement process prior to the award of contract; and - the Employer’s decision to award the contract. |

Section III – Evaluation and Qualification Criteria

Section III - Evaluation and Qualification Criteria

This section contains all the criteria that the Employer shall use to evaluate Proposals and qualify Proposers.  No other factors, methods or criteria shall be used other than specified in this document. The Proposer shall provide all the information requested in the forms included in Section IV, Proposal Forms.

Wherever a Proposer is required to state a monetary amount, Proposers should indicate the USD equivalent using the rate of exchange determined as follows:

- For construction turnover or financial data required for each year - Exchange rate prevailing on the last day of the respective calendar year (in which the amounts for that year is to be converted) was originally established.

- Value of single contract - Exchange rate prevailing on the date of the contract.

Exchange rates shall be taken from the publicly available source identified in the ITP 38.1. Any error in determining the exchange rates in the Proposal may be corrected by the Employer.

- Technical and Financial Evaluation

- Evaluation of Technical Proposal

Assessment of adequacy of Technical Proposal with Requirements in accordance with ITP 31.2 detailed via 3.0 Qualification: Qualification Criteria and Requirements under this section will be used to evaluate the technical Proposals on a pass/fail basis.

1.1 Techinical Proposal Scoring Methology ( Not Applicable)

If as per ITP 31.2, the technical factors (and sub- factors, if applicable) are weighted in terms of relevance, the total technical score would be the weighted average in percent.

The score for each sub- factor (i) within a factor (j) will be combined with the scores of sub- factors in the same factor as a weighted sum to form the Factor Technical Score using the following formula:

where:

tji	= the technical score for sub- factor “i” in factor “j”,

wji	= the weight of sub- factor “i” in factor “j”,

k	= the number of scored sub-factors in factor “j”, and

The Factor Technical Scores will be combined in a weighted sum to form the total Technical Proposal Score using the following formula:

where:

Sj	= the Factor Technical Score of factor “j”,

Wj	= the weight of factor “j” as specified in the PDS,

n	= the number of Factors, and

- 1.2 Sustainable Procurement ( Not Applicable)

1.3 Alternative Technical Solutions for specified parts of the Works  ( Not Applicable)

- Financial Evaluation

2.1 Margin of Preference ( Not Applicable)

If the PDS so specifies, the Employer will grant a margin of preference of 7.5% (seven and one-half percent) to domestic contractors, in accordance with, and subject to, the following provisions:

(i)	Contractors applying for such preference shall be asked to provide, as part of the data for qualification, such information, including details of ownership, as shall be required to determine whether, according to the classification established by the Borrower and accepted by the Bank, a particular contractor or group of contractors qualifies for a domestic preference. The Bidding document shall clearly indicate the preference and the method that will be followed in the evaluation and comparison of Proposals to give effect to such preference.

(ii)	After Proposals have been received and reviewed by the Employer, responsive Proposals shall be classified into the following groups:

(a)	Group A: Proposals offered by domestic contractors eligible for the preference.

(b)	Group B: Proposals offered by other contractors.

All evaluatedProposals in each group shall, as a first evaluation step, be compared to determine the Most Advantageous Bid, and the Most Advantageous Proposalin each group shall be further compared with each other. If a result of this comparison, a Proposal from Group A is the Most Advantageous Bid, it shall be selected for the award, if the Proposer is qualified. If a Proposalfrom Group B is the Most Advantageous Bid, as a second evaluation step, all Proposals from Group B shall then be further compared with the Most Advantageous Proposalfrom Group A. For the purpose of this further comparison only, an amount equal to 7.5% (seven and one-half percent) of the respective Proposalprice corrected for arithmetical errors, including unconditional discounts but excluding provisional sums and the cost of day works, if any, shall be added to the evaluated cost offered in each Proposalfrom Group B. If the Proposalfrom Group A is the Most Advantageous Bid, it shall be selected for award. If not, the most advanatgeous Proposalfrom Group B based on the first evaluation step shall be selected.

2.2 Criteria for Financial Evaluation

In addition to the criteria listed in ITP 40.1 (a) – (f) the following criteria shall apply:

#### Time Schedule (Not Applicable)

Time for completion of the Works from the Commencment Date shall be as specified in the Particular Conditions Part A-Contract Data Sub-clause 1.1.84.  No credit will be given for earlier completion.

Or

Time to complete the Works from the from the Commencment Date shall be between ____________ minimum and ____________ maximum. The adjustment rate in the event of completion beyond the minimum period shall be _______ (%) for each week of delay from that minimum period. No credit will be given for completion earlier than the minimum designated period. Proposals offering a completion date beyond the maximum designated period shall be rejected.

#### Life Cycle Costs

The factors for calculation of the life cycle cost are:

      - number of years for life cycle: 10 years

      - For power costs, Amount of required electricity consumption for operation of the STP as specified in functional guarantee by proposer. Unit rate of 6.65 Maldivain Ruffiya per kWh shall be included in the Proposed price and indicated separately from other cost. At the time of the Contract signing, the electrical cost for Operation Service will be recalculated based on prevailing Government rate during negotiation and amended in the Contract with new rate.

The bidder’s statement of electricity consumption will be verified by manufacturer’s certifications, literature, catalogue, efficiency curves of pumps. Inconsistencies and errors will be rectified.

      - operating costs derived from Part [2] Proposal Price Forms – Operation Service Summary for Operation Service

      - maintenance costs, including the cost of spare parts for the period of operation should be included in the Price proposal, and

      - Discount rate: 9% to be used to discount to present value all annual future costs calculated under (ii) and (iii) above for the period specified in (i).

      - Other than cost for power, chemical and annual cost of operation as proposed in the financial proposal shall be extended as 10 years under the assumption of full capacity operation as design capacity. The proposed cost shall include all other possible cost required for operation of the plant based on Employer’s requirement. Prior to the financial evaluation, the Employer may request required document as proof of the proposed operation cost. If those cost are not reasonable in the local context, revision of the price according to Employer’s understanding shall be made.

#### Net Present Valuation of Proposer’s Financial Part

The Design-Build Proposal Price shall not be discounted.

If the PDS provides for Net Present Valuation of the Operation Service Proposal Price, the annual amounts in the Operation Service price schedules, as adjusted in accordance with ITP 40.1 (a) to (e), shall be discounted using a discount factor of 9% ( Maldives Monitory Authority, Economic Update MAech 2021, Volume 3 Issue 3). The discount base year shall be the year preceding the first year of the Operation Service Period.

For greater certainty, net present values shall be determined by applying the following discount factors to the annual amounts in the Proposal forms during the Operation Service Period.

| Operation Period | Discount factor to be applied | Operation Period | Discount factor to be applied |
| --- | --- | --- | --- |
| Year 1 | 0.971 | Year 9 | 0.460 |
| Year 2 | 0.842 | Year 10 | 0.422 |
| Year 3 | 0.772 |  |  |
| Year 4 | 0.708 |  |  |
| Year 5 | 0.650 |  |  |
| Year 6 | 0.596 |  |  |
| Year 7 | 0.547 |  |  |
| Year 8 | 0.502 |  |  |

P/given F formula

P = F / (1+i)n

where

P = Present value	n = Year

F = Future values	i = Discount rate (9%)

- Combined Evaluation ( Not Applicable)

The Employer will evaluate and compare the Proposals that have been determined to be substantially responsive.

An Evaluated Proposal Score (B) will be calculated for each responsive Proposal using the following formula, which permits a comprehensive assessment of the evaluated cost and the technical merits of each Bid:

Where:

C		= Evaluated ProposalCost

C low	= the lowest of all Evaluated ProposalCosts among responsive Proposals

T	   	= the total Technical Score awarded to the Bid

Thigh	= the Technical Score achieved by the Proposal that was scored best among all responsive Proposals

X		= weight for Cost as specified in the PDS

The Proposal with the best evaluated Proposal Score (B) among responsive Proposals shall be the Most Advantageous Proposal provided the Proposer is qualified to perform the Contract.

- Multiple Contracts ( Not Applicable)

- Specialized Subcontractors (Not Applicable)

3.0 Qualification: Qualification Criteria and Requirements

[Note to Employer: Only applications that are substantially responsive to the qualification criteria and requirements in Table 1 are to be assessed against Table 2, Rated Criteria and Requirements.]

| Eligibility |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Criteria |  |  |  |  | Single Entity Requirements |  | Joint Venture |  |  |  |  | Documentation |  |
| No. |  | Subject |  | Requirement |  |  | All Members Combined |  | Each Member | One Member |  | Submission Requirements |  |
| 1.1 | Nationality |  | Nationality in accordance with ITP 4.4 |  | Must meet requirement | Must meet requirement |  | Must meet requirement |  |  | N/A |  | Forms ELI – 1.1 and 1.2, with attachments |  |
| 1.2 | Conflict of Interest |  | No conflicts of interest in accordance with ITP 4.2 |  | Must meet requirement | Must meet requirement |  | Must meet requirement |  |  | N/A |  | Application Submission Letter |  |
| 1.3 | Bank Eligibility |  | Not having been declared ineligible by the Bank, as described in ITP 4.1 and 5.1 |  | Must meet requirement | Must meet requirement |  | Must meet requirement |  |  | N/A |  | Application Submission Letter |  |
| 1.4 | United Nations resolution or Borrower’s country law |  | Not having been excluded as a result of prohibition in the Borrower’s country laws or official regulations against commercial relations with the Applicant’s country, or by an act of compliance with UN Security Council resolution, both in accordance with ITP 5.1 and Section V. |  | Must meet requirement | Must meet requirement |  | Must meet requirement |  |  | N/A |  | Forms ELI – 1.1 and 1.2, with attachments |  |

| Historical Contract Non-Performance |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Criteria |  |  | Single Entity Requirements | Joint Venture |  |  | Documentation |
| No. | Subject | Requirement |  | All Members Combined | Each Member | One Member | Submission Requirements |
| 2.1 | History of Non-Performing Contracts | Non-performance of a contract did not occur as a result of contractor’s default since 1st January 2016. | Must meet requirement | Must meet requirements | Must meet requirement | N/A | Form CON-2 |
| 2.2 | Suspension Based on Execution of Proposal or Proposal Securing Declaration by the Employer | Not under suspension based on execution of Proposal or Proposal Securing Declaration pursuant to ITP 4.7 | Must meet requirement | Must meet requirement | Must meet requirement | N/A | Application Submission Letter |
| 2.3 | Pending Litigation | Applicant’s financial position and prospective long-term profitability still sound according to criteria established in 3.1 below and assuming that all pending litigation will be resolved against the Applicant | Must meet requirement | N/A | Must meet requirement | N/A | Form CON – 2 |
| 2.4 | Litigation History | No consistent history of court/arbitral award decisions against the Applicant since 1st January 2016 | Must meet requirement | Must meet requirement | Must meet requirement | N/A | Form CON – 2 |
| 2.5 | Declaration: Environmental and Social (ES) past performance | Declare any civil work contracts that have been suspended or terminated and/or performance security called by an employer for reasons related to the non-compliance of any environmental, or social (including Sexual Exploitation and Abuse) contractual obligations in the past five years. (January 2016) | Must make the declaration. Where there is Sub-contractor/s such Sub-contractor/s must make the declaration. | N/A | Each must make the declaration. Where there is Sub-contractor/s such Sub-contractor/s must make the declaration. | N/A | Form CON-3 ES Performance Declaration |

| Financial Situation and Performance |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Criteria |  |  | Single Entity Requirements | Joint Venture Requirements |  |  | Documentation |
| No. | Subject | Requirement |  | All Members Combined | Each Member | One Member | Submission Requirements |
| 3.1 | Financial Capabilities | - The Proposer shall demonstrate that it has access to, or has available, liquid assets, unencumbered real assets, lines of credit, and other financial means (independent of any contractual advance payment) sufficient to meet the cash flow requirements estimated as US $ 875,000 for the subject contract net of the Applicants other commitments. - The Proposer shall also demonstrate, to the satisfaction of the Employer, that it has adequate sources of finance to meet the cash flow requirements on contracts currently in progress and for future contract commitments. - The audited financial statements or, if not required by the laws of the Applicant’s country, other financial statements acceptable to the Employer, for the last 5 five years shall be submitted and must demonstrate the current soundness of the Applicant’s financial position and indicate its prospective long-term profitability. | Must meet requirement Must meet requirement Must meet requirement | Must meet requirement Must meet requirement N/A | 25 % of the requirement Must meet requirement Must meet requirement | Must meet 40 % of the requirement N/A N/A | Form FIN – 3.1, with attachments |
| 3.2 | Average Annual Turnover | - Minimum average annual turnover of US$ Fourteen (14.0) Million or equivalent calculated as total certified payments received for contracts in progress and/or completed within the last Five (5) years. | Must meet requirement | Must meet requirement | N/A | Lead member must meet Seventy (70) %, of the requirement | Form FIN – 3.2 |

| Experience |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Criteria |  |  | Single Entity Requirements | Joint Venture Requirements |  |  | Documentation |
| No. | Subject | Requirement |  | All Members Combined | Each Member | One Member | Submission Requirements |
| 4.1 | DBO Experience | ### For the purpose of determining a Proposer’s compliance with the qualification criteria a Sewage Treatment Plant (STP) means a treatment facility designed, developed and constructed, and operated for primary and secondary treatment of sewage for its safe disposal complying with the regulatory norms. Waste stabilization pond / other pond process will not be covered under this definition. - The Proposer has successfully completed One (1) sewage treatment plant of Eight (8) MLD capacity OR Two (2) of Minimum 5 MLD Capacity OR Three(3) of Minimum 4 MLD Capacity between January 2010 and Application Deadline. The selected DBO contracts shall relate to treatment plant that: The selected DBO contracts shall: - Have been satisfactorily completed. - have been operating for at least two (2) years since commissioning, and - have been operating satisfactorily since commissioning. - The Proposer shall also provide evidence that the treatment technology proposed for this contract has been adopted (not necessarily built by the Proposer) in at least 3 locations during last 10 years and that such STP has been operating successfully (meeting the required performance standards) for a period of minimum 3 years over a period of last 10 years. | Must meet the requirements Must meet requirement Must meet requirement | Must meet the requirements Must meet requirement N/A | N/A N/A | Must meet the requirements N/A Must meet requirement | Form EXP - 4.1 Form EXP - 4.3 |
| 4.2 | Design Experience | A minimum number of one (1) projects for the design of wastewater treatment plants undertaken between 1st January 2010 and Application submission deadline. The selected design contracts shall relate to treatment plant that: - have been satisfactorily completed, and - each have a minimum design of sewage treatment plant of Four (4) MLD capacity | Must meet requirement | N/A | N/A | Must meet requirement | Form EXP - 4.2 |
| 4.4 | Operations experience | - A minimum number of Two (2) Operations contracts for sewage treatment plants that have been operating satisfactorily since commencement as a prime contractor, joint venture member, management contractor or subcontractor between 1st January 2010 and Application submission deadline. The selected operations contracts: - Shall relate to treatment plant with at least One (1) sewage treatment plant of Eight (8) MLD capacity OR Two (2) of Minimum 5 MLD Capacity OR Three(3) of Minimum 4 MLD Capacity between January 2010 and Application Deadline. - Shall have a contract period of two years or more - Shall have been operating satisfactorily since commencement - The Proposer shall provide evidence that it has the experience in operating and maintaining successfully at least One (1) project for an odour control and In-Vessel Sludge Composting Plant to compost the daily production of dewatered sludge from the STP as described in Part 2: Employers Requirement (1.2.2) | Must meet requirement Must meet requirement | N/A N/A | N/A N/A | Lead member must meet requirement Must meet requirement | Form EXP - 4.4 |
| 4.5 | Specific Experience in managing ES aspects | Minimum Two (2) projects implemented with since 2010 with all the environmental and social safeguards risk mitigated and managed. Minimum One (1) projects with odor control systems designed and implemented effectively. | Must meet requirement | Must meet requirement | N/A | N/A | Form EXP – 4.5 |

- Contractor’s Representative and Key Personnel

The Proposer must demonstrate that it will have a suitably qualified Contractor’s Representative and sufficient suitably qualified Key Personnel as are required to perform the Contract. This should be in line with Part 2: Employers Requirement Clause 8.1

The Proposer shall provide details of the Contractor’s Representative and such other Key Personnel that the Proposer considers appropriate, together with their academic qualifications and work experience. The Proposer shall complete the relevant Forms in Section IV, Proposal Forms.

The Contractor shall not, without the prior consent of the Employer’s Representative substitute or replace the Contractor’s Representative (reference General Conditions of Contract 4.3) or any of the Key Personnel (reference the Particular Conditions of Contract 6.9).

The minimum qualifications and experience of the Contractor’s Representative and Key Personnel are set out in the Employer’s Requirements.

- Equipment

The Proposer shall provide its strategy for acquiring and maintaining the key equipment that may be needed to perform the Contract.

The Proposer shall provide further details of proposed items of equipment using the relevant Form in Section IV.

While this is a Design, Build and Operate (DBO) project and the proposer shall design and propose equipment that best suits their design and meet the employer’s requirement, at a minimum the proposed equipment should include (list detailed is only suggestive and proposer to suggest quipment as needed for their process:

| Item No. | Description of Item | Minimum Criteria to be Met |
| --- | --- | --- |
| 1 | Pumps | Standard pumping equipment from reputable manufacturer with at least ten (10) years successful experience in the design, fabrication and supply of this kind and size of equipment. |
| 2 | Screen | A single manufacturer shall furnish all equipment with at least ten (10) years successful experience in the design, fabrication and supply of this kind and size of equipment |
| 3 | Biological Treatment Technology based on design of proposer | Reputable manufacturer shall furnish Biological Treatment Equipment as per chosen technology with at least ten (10) years successful experience in the design, fabrication and supply of this kind and size of equipment. |
| 4 | Sludge Thickening (if any) and Sludge Dewatering Equipment | Manufacturer/supplier shall have a minimum of 10 years’ experience in the design, fabrication and supply of digester installations, thickening & dewatering machines and have delivered at least for one (1) large STP serving 50,000 people equivalents during the last three (3) years. |
| 5 | Wastewater Effluent Disinfection | All equipment shall be produced by reputable manufacturer with minimum of 10 years’ experience in the design, fabrication and supply of this kind and size of equipment. |
| 6 | SCADA Monitoring & Control System a) Hardware and b) Software | SCADA system, which may be subdivided in a) and b), shall be provided by suppliers with minimum of 10 years’ experience in the design, fabrication and supply of similar SCADA Systems for Water or Waste Water Treatment plants. SCADA should be capable of measuring sewage flows to the treatment plant and influent and effluent characteristics (pH, Suspended solids, COD and BOD |
| 7 | Diesel Engine Driven Emergency Generator | The generator for emergency power supply of the STP shall be standard product of a manufacturer with minimum of 10 years’ experience in the design, fabrication and supply of this kind and size of equipment. |
| 8 | Civil Works, Mechanical and Electrical Installation or other subcontractors | Proposer for any civil work must have at least 10 years’ experience in similar works the Subcontractor is intended to carry out. Major civil works are listed below: - soil stabilization/piling - earth and excavation, backfilling and compaction works - concrete tanks and structures - fencing - road works - Mechanical and electrical Installation - Piping - Steelworks |
| 11 | Manufactures of any other Mechanical, electrical and instrumentation equipment not listed above (Bio filter, odor control system, in vessel composting, etc) | A reputable manufacturer shall furnish all equipment with at least ten (10) years successful experience in the design, fabrication and supply of this kind and size of equipment. |

General notes for the Applicant:

- The Applicant may use a single contract to satisfy two or more criteria requirements. In such cases, the Applicant shall complete separate EXP forms for each subject contract type. (For example, if a contractor undertook both design and construction on a similar contract, it may use that experience to qualify under Design Experience and Construction Experience. It such case it would complete forms EXP-4.2 and EXP-4.3.)

- For contracts under which the Applicant participated as a joint venture member or sub-contractor, only the Applicant’s role and responsibilities shall be considered as qualifying experience.

Section IV – Proposal Forms

Table of Forms

Qualification: Rated Criteria and Requirements ( Table 2)	65

Letter of Proposal - Technical Part	69

Letter of Proposal - Financial Part	72

Appendix to Proposal	75

Schedule of Adjustment Data	75

Table A. Design-Build Local Currency	75

Table B. Design-Build Foreign Currency (FC)	76

Table C. Summary of Payment Currencies (Design Build)	77

Table D Schedule of Adjustment Data for the Operation Service	78

Table E Schedule of Adjustment Data for the Asset Replacement Fund (need to fill)	80

Schedule of Priced Activities and Sub-activities	81

Sample Schedule of Priced Activities Table (may need to be revisited)	82

Sample Schedule of Priced Sub- activities Table	83

Specified Provisional Sums	84

Summary (Design-Build)	85

Operation Service Fees (excl. Asset Replacement Fund)	86

Asset Replacement Schedule	87

Summary for Operation Service	88

Part 3: Grand Summary	89

Technical Proposal Forms	90

Design Methodology	92

Construction Management Strategy	1-93

Design Build. Method Statements for key construction activities	1-94

Code of Conduct for Contractor’s Personnel (ES) Form	1-95

Design Build Work Program	1-99

Design Build Personnel Organization Chart	1-100

Operation Service Proposals	1-101

Form EQU. Contractor’s Equipment	1-102

Form PER -1. Contractor’s Representative and Key Proposed Personnel	1-102

Form PER-2. Resume and Declaration of Contractor’s Representative and Key Personnel	1-105

Risk assessment	1-107

Proposed Subcontractors for Major Activities/Sub-Activities	1-108

Qualification Forms	1-109

Form ELI 1.1. Proposer Information Sheet	1-110

Form ELI 1.2.  Party to JV Information Sheet	1-111

Form CON – 2.  Historical Contract Non-Performance, and Pending Litigation	1-112

Form CON – 3. Environmental and Social Performance Declaration	1-114

Form CCC Current Contract Commitments / Works in Progress	1-116

Form FIN – 3.1: Financial Situation and Performance	1-117

Form FIN - 3.2: Average Annual Construction Turnover	1-119

Form FIN 3.3. Financial Resources	1-120

Form EXP - 4.1: Specific DBO Experience	1-121

Form EXP - 4.2: Specific Design Experience	1-123

Form EXP - 4.3: Specific Construction Experience	1-125

Form EXP - 4.4: Specific Operations Experience	1-127

Form EXP - 4.5 : Specific Experience in Managing ES aspects	1-129

Others	1-130

Form of Proposal Security – Demand Guarantee	1-131

Form of Proposal-Securing Declaration	1-133

FORM OF POWER OF ATTORNEY FOR JOINT VENTURE	1-134

Letter of Proposal - Technical Part

INSTRUCTIONS TO PROPOSERS

INSTRUCTIONS TO PROPOSERS: DELETE THIS BOX ONCE YOU HAVE COMPLETED THE DOCUMENT Place this Letter of Proposal in the first envelope “TECHNICAL PART”. The Proposer must prepare the Letter of Proposal on stationery with its letterhead clearly showing the Proposer’s complete name and business address. Note: All italicized text in black font is to help Proposers in preparing this form and Proposers shall delete it from the final document.

Date of this Proposal submission: [insert date (as day, month and year) of Proposal submission]

RFP No.: [insert number of RFP process]

Request for Proposal No.: [insert identification]

Alternative No.: [insert identification No if this is a Proposal for an alternative]

To: [Employer insert: name and address of Employer]

Dear Sir or Madam:

We, the undersigned Proposer, hereby submit our Proposal, in two parts, namely:

- the Technical Part, and

- The Financial Part.

Having examined the RFP Documents including any Addenda issued in accordance with ITP 8, we, the undersigned, offer to provide the Works and Operation Service, in full conformity with the said RFP Documents and any Addenda.

We undertake, if our Proposal is accepted, to commence the Works and achieve Completion within the respective times stated in the RFP Documents.

We hereby certify that we, including any subcontractors or manufacturers for any part of the contract, meet the eligibility requirements and have no conflict of interest in accordance with ITP 4.

We, along with any of our subcontractors, suppliers, consultants, manufacturers, or service providers for any part of the contract, are not subject to, and not controlled by any entity or individual that is subject to, a temporary suspension or a debarment imposed by the World Bank Group or a debarment imposed by the World Bank Group in accordance with the Agreement for Mutual Enforcement of Debarment Decisions between the World Bank and other development banks. Further, we are not ineligible under the Employer’s Country laws or official regulations or pursuant to a decision of the United Nations Security Council;

We hereby certify that we have taken steps to ensure that no person acting for us or on our behalf engages in any type of Fraud and Corruption.

State-owned enterprise or institution: [select the appropriate option and delete the other] [We are not a state-owned enterprise or institution] / [We are a state-owned enterprise or institution but meet the requirements of ITP 4.6];

Potential DAB Members: We hereby propose the following three persons, whose curriculum vitae are attached, as potential DAB members:

| Name | Address |
| --- | --- |
| - ………… |  |
| - ………… |  |
| - ………… |  |

We agree to abide by this Proposal, which, in accordance with ITP 12 and ITP 13, consists of this letter (Letter of Proposal - Technical Part) and enclosures, until [ insert day, month and year in accordance with PDS 20.1], and it shall remain binding upon us and may be accepted by you at any time on or before this date..

Until the formal final Contract is prepared and executed between us, this Proposal, together with your written acceptance thereof included in your Letter of Acceptance, shall constitute a binding contract between us.

Name of the Proposer: *[insert complete name of  the Proposer]

Name of the person duly authorized to sign the Proposal on behalf of the Proposer: 
** [insert complete name of person duly authorized to sign the Proposal]

Title of the person signing the Proposal: [insert complete title of the person signing the Proposal]

Signature of the person named above: [insert signature of person whose name and capacity are shown above]

Date signed [insert date of signing] day of [insert month], [insert year]

*: In the case of the Proposal submitted by a Joint Venture specify the name of the Joint Venture as Proposer.

**: Person signing the Proposal shall have the power of attorney given by the Proposer. The power of attorney shall be attached with the Proposal Schedules.

ENCLOSURE(S):

Letter of Proposal - Financial Part

INSTRUCTIONS TO PROPOSERS

INSTRUCTIONS TO PROPOSERS: DELETE THIS BOX ONCE YOU HAVE COMPLETED THE DOCUMENT Place this Letter of Proposal in the second envelope “FINANCIAL PART”. The Proposer must prepare the Letter of Proposal on stationery with its letterhead clearly showing the Proposer’s complete name and business address. Note: All italicized text in black font is to help Proposers in preparing this form and Proposers shall delete it from the final document.

Date of this Proposal submission: [insert date (as day, month and year) of Proposal submission]

RFP No.: [insert number of RFP process]

Request for Proposal No.: [insert identification]

Alternative No.: [insert identification No if this is a Proposal for an alternative]

To: [Employer insert: name and address of Employer]

Dear Sir or Madam:

We, the undersigned Proposer, hereby submit the second part of our Proposal, the Financial Part

Having examined the RFP Documents including any Addenda issued in accordance with ITP 8, we, the undersigned, offer to provide the Works and Operation Service to Design, Build and operation 10 MLD STP in Hulumalé Phase 1, in full conformity with the said RFP Documents and any Addenda for the total Proposal Price, excluding any discounts offered below is

- [Insert one of the options below as appropriate]

Option 1, in case of one lot: Total price is: [insert the total price of the Proposal in words and figures, indicating the various amounts and the respective currencies];

Or

Option 2, in case of multiple lots: (a) Total price of each lot [insert the total price of each lot in words and figures, indicating the various amounts and the respective currencies]; and (b) Total price of all lots (sum of all lots) [insert the total price of all lots in words and figures, indicating the various amounts and the respective currencies];

The discounts offered and the methodology for their application is:

(i)	The discounts offered are: [Specify in detail each discount offered]

(ii)	The exact method of calculations to determine the net price after application of discounts is shown below: [Specify in detail the method that shall be used to apply the discounts];

If our Proposal is accepted, we undertake to provide an advance payment security and a Performance Security and an Environmental and Social (ES) Performance Security in the form, in the amounts, and within the times specified in the RFP Documents.

We agree to abide by this Proposal, which, in accordance with ITP 12 and ITP 13, consists of this letter (Letter of Proposal – Financial Part) and the enclosures listed below, until [ insert day, month and year in accordance with PDS 20.1], and it shall remain binding upon us and may be accepted by you at any time on or before this date..

Commissions, gratuities and fees: We have paid, or will pay the following commissions, gratuities, or fees with respect to the RFP process or execution of the Contract: [insert complete name of each Recipient, its full address, the reason for which each commission or gratuity was paid and the amount and currency of each such commission or gratuity].

| Name of Recipient | Address | Reason | Amount |
| --- | --- | --- | --- |

(If none has been paid or is to be paid, indicate “none.”)

Until the formal final Contract is prepared and executed between us, this Proposal, together with your written acceptance thereof included in your Letter of Acceptance, shall constitute a binding contract between us.

Name of the Proposer:*[insert complete name of the Proposer]

Name of the person duly authorized to sign the Proposal on behalf of the Proposer: ** [insert complete name of person duly authorized to sign the Proposal]

Title of the person signing the Proposal: [insert complete title of the person signing the Proposal]

Signature of the person named above: [insert signature of person whose name and capacity are shown above]

Date signed [insert date of signing] day of [insert month], [insert year]

*: In the case of the Proposal submitted by a Joint Venture specify the name of the Joint Venture as Proposer.

**: Person signing the Proposal shall have the power of attorney given by the Proposer. The power of attorney shall be attached with the Proposal Schedules.

ENCLOSURE(S):

Appendix to Proposal

Schedule of Adjustment Data (Not Applicable)

[Design Build of the Works]

[In Tables A, B, and C, below, the Proposer shall (a) indicate its amount of local currency payment, (b) indicate its proposed source and base values of indices for the different foreign currency elements of cost, (c) derive its proposed weightings for local and foreign currency payment, and (d) list the exchange rates used in the currency conversion. In the case of very large and/or complex works contracts, it may be necessary to specify several families of price adjustment formulae corresponding to the different works involved.]

Table A. Design-Build Local Currency

| Index code* | Index description* | Source of index* | Base value and date* | Proposer’s related currency amount | Proposer’s Proposed weighting |
| --- | --- | --- | --- | --- | --- |
|  | Nonadjustable | — | — | — | A: * B: * C: * D: * E: * |
|  |  |  | Total |  | 1.00 |

[* To be entered by the Employer. Whereas “A” should a fixed percentage, B, C, D and E should specify a range of values and the Proposer will be required to specify a value within the range such that the total weighting = 1.00]

Table B. Design-Build Foreign Currency (FC)

State type: 	[If the Proposer is allowed to receive payment in foreign currencies this table shall be used. If Proposer wishes to quote in more than one foreign currency (up to three currencies permitted) then this table should be repeated for each foreign currency.]

| Index code | Index description | Source of index | Base value and date | Proposer’s related source currency in type/amount | Equivalent in FC1 | Proposer’s proposed weighting |
| --- | --- | --- | --- | --- | --- | --- |
|  | Nonadjustable | — | — | — |  | A: * B: * C: * D: * E: * |
|  |  |  |  | Total |  | 1.00 |

[* To be entered by the Employer. Whereas “A” should a fixed percentage, B, C, D and E should specify a range of values and the Proposer will be required to specify a value within the range such that the total weighting = 1.00]

Table C. Summary of Payment Currencies (Design Build)

[Table: Alternative B]

To be used only with Alternative B Prices directly quoted in the currencies of payment. (ITP 16.1)

Summary of currencies of the Proposal for:	 [insert name of Section of the Works]

| Name of currency | Amounts payable |
| --- | --- |
| Local currency: |  |
| Foreign currency #1: |  |
| Foreign currency #2: |  |
| Foreign currency #3: |  |
| Provisional sums expressed in local currency | [To be entered by the Employer] |

Table D
Schedule of Adjustment Data for the Operation Service (Not Applicable)

(excluding Asset Replacement)

[In Tables D1, D2 etc., below, the Proposer shall (a) indicate its proposed source and base values of indices for the different local and foreign currency elements of cost, (b) specify its proposed weightings for local and foreign currency payment.]

Table D1. Operation Service- Fee Component 1

| Name of currency component | Rate of exchange at base date (Local currency per unit of foreign) | Name and source of index | Base value of index at Base Date | Proposer’s Proposed index weighting (%) [at base date] |
| --- | --- | --- | --- | --- |
| [insert name of local currency] |  | [Insert name of index(es)] |  | b= |
|  |  |  |  | c= |
|  |  |  |  | d= |
| [Insert name of Foreign Currency #1] |  |  |  | w= |
| [Insert name of Foreign Currency #2] |  |  |  | y= |
| [Insert name of Foreign Currency #3] |  |  |  | z= |
|  |  |  | Total | 100% |

Table D2. Operation Service- Variable Fee (Not Applicable)

| Name of currency component | Rate of exchange at base date (Local currency per unit of foreign) | Name and source of index | Base value of index at Base Date | Proposer’s Proposed index weighting (%) [at base date] |
| --- | --- | --- | --- | --- |
| [insert name of local currency] |  | [Insert name of index(es)] |  | b= |
|  |  |  |  | c= |
|  |  |  |  | d= |
| [Insert name of Foreign Currency #1] |  |  |  | w= |
| [Insert name of Foreign Currency #2] |  |  |  | y= |
| [Insert name of Foreign Currency #3] |  |  |  | z= |
|  |  |  | Total | 100% |

Notes for the Employer:

1)	For simplicity the table allows only one index per foreign currency. Additional rows can be added if the Employer intends to permit Proposers to use multiple indexes per currency in which case the formula in the Schedule of Indexation will also require adjustment.

2)	Additional tables (D2, D3 etc.) should be added for each component of the Operation Service Fee. For example, if the contractor is paid a fixed fee and a variable fee, two tables may be required; one table covering the fixed fee and the other covering the variable fee.

3)	It is normally not necessary to have a non-adjustable component during the Operation Service Period.]

Table E
Schedule of Adjustment Data for the Asset Replacement Fund

[In Tables E1 etc., below, the Proposer shall indicate source and base values of indices for the different foreign currency elements of cost included in its Asset Replacement Schedule.]

Table E1. Asset Replacement

| Name of currency | Rate of exchange at Base Date (Local currency per unit of foreign) | Name and source of index | Base value of index at Base Date |
| --- | --- | --- | --- |
| [insert name of local currency] |  | [Insert name of index(es)] |  |
| [Insert name of Foreign Currency #1] |  |  |  |
| [Insert name of Foreign Currency #2] |  |  |  |
| [Insert name of Foreign Currency #2] |  |  |  |

[Notes for the Employer:

1)	To be adapted by the Employer to suit its proposed Asset Replacement Proposal forms, Proposal currency requirements, and adjustment provisions.

2)	For simplicity the table shows only one index per currency. Additional rows can be added if the Employer intends to permit Proposers to use multiple indexes per currency. In such cases, the Proposer should be required to provide index weightings for each currency.

3)	The Employer shall note that the currency and index weighting may be different for each asset to be replaced. Therefore, there is no provision for the Proposer to specify its proposed weighting in this table

4)	It is normally not necessary to have a non-adjustable component for the Asset Replacement Fund.]

Schedule of Priced Activities and Sub-activities

The total of the prices of the activities in the Schedule of Priced Activities is the Proposer’s offer to complete the works on a “single responsibility” basis.

The cost of any activity or sub-activity that the Proposer may have omitted is deemed to be included in the price of other activities or sub-activities in the Schedule of Priced Activities and Sub-activities  and will not be paid for separately by the Employer.

The priced activity and sub activity schedules provided by the Proposer will be used for Proposal evaluation. These schedules together with the work program serve as a basis for estimating the instalments in the Schedule of Payments. Therefore, the proposer should prepare work program in details to be coordinated with submitted schedule.

If total sum of each price activity exceed indicated percentage, breakdown of detailed rate will be requested for adjustment of correction if the proposer is selected as most advantageous proposal.

| Activities | Minimum or maximum ratio |
| --- | --- |
| Design | Maximum 3% of Total Bid Price |
| Equipment | Between 35 ~ 45% of Total Bid Price |
| Construction | Between 40 ~ 50% of Total Bid Price |
| Operation (10 years) | Minimum 15% of Total Bid Price |

For unbalanced or front-loaded proposal, the Employer had right to reject the proposal based on Clause 5.64 from “Procurement Regulation for IPF Borrowers”.

5.64. For Works and Plant, if the Bid/Proposal that results in the lowest evaluated cost/best evaluated Proposal is, in the Borrower’s opinion, seriously unbalance or front-loaded, the Borrower may require the Bidder/Proposer to provide written clarifications, including detailed price analyses to demonstrate the consistency of the prices with the scope of Works, proposed methodology, and schedule. After evaluation the detailed price analyses (for contracts subject to prior review, with the Bank’s no-objection), the Borrower may as appropriate:

a. accepts the Bid/Proposal:

b. requires that the total amount of the performance security be increased, at the expense of the Bidder/Proposer, to a level not exceeding twenty percent (20%) of the contract price: or

c. reject the bid/Proposal

Part [1] Proposal Price Forms - Design-Build.

Sample Schedule of Priced Activities Table

[To be completed by the Proposer (more tables to be used by the Proposer as appropriate in relation to the Employers Requirement)]

| Activity No. | Description of Activity | Activity Price |
| --- | --- | --- |
| 1. | Design, Documentation and Submittals |  |
| 2. | Mobilization & Site Preparation |  |
| 3. | Construction-Civil Works |  |
| 4. | Mechanical & Electrical. Instrumentation Plant and Equipment for Incorporation in the Permanent Works (including trial run ) |  |
|  | Total price of Activities carried forward to Grand Summary, Page ____ |  |

Part [1] Proposal Price Forms - Design-Build

Sample Schedule of Priced Sub- activities Table

[To be completed by the Proposer (more tables to be used by the Proposer as appropriate in relation to the Employers Requirement)]

Activity 1: Design and Documentation

| Sub-activity No. | Description of Sub-activity | Sub-activity Price |
| --- | --- | --- |
| 1.1 | Survey and Investigation |  |
| 1.1.a | Topographical Survey |  |
| 1.1.b | Soil Investigation |  |
| 1.1.c | ……. |  |
| 1.2 | Detailed Design |  |
| 1.3 | Process Design |  |
| 1.3.a | ……. |  |
| 1.4 | M&E Design |  |
| 1.4.a | ……. |  |
| 1.5 | Architectural Design |  |
| 1.5.a | …………. |  |
|  | Others |  |
|  | ----------(Bidders to add as required) |  |
|  | Total price of Sub-activities carried forward to the Priced Activity Schedule, Page ____ |  |
|  | Total price of Sub-activities in words carried forward to the Priced Activity Schedule, Page ____ |  |

Part [1] Proposal Price Forms - Design-Build

Sample Schedule of Priced Sub- activities Table

[To be completed by the Proposer (more tables to be used by the Proposer as appropriate in relation to the Employers Requirement)]

Activity 2: Mobilization and Submittals

| Sub-activity No. | Description of Sub-activity | Sub-activity Price |
| --- | --- | --- |
| 2.1 | Mobilization: Preparation of construction site. mobilization of contractor’s site staff, topographical surveys, subsoil investigation, contractor’s and employer’ office and utility connections &etc. |  |
| 2.2 | Submittals: Contractor’s programme, Project specific quality plan(D&B), Occupational Health, Safety and Environmental Management Plan and Others as specified in the Contract. |  |
|  | ----------(Bidders to add as required) |  |
|  | Total price of Sub-activities carried forward to the Priced Activity Schedule, Page ____ |  |
|  | Total price of Sub-activities in words carried forward to the Priced Activity Schedule, Page ____ |  |

Part [1] Proposal Price Forms - Design-Build

Sample Schedule of Priced Sub- activities Table

[To be completed by the Proposer (more tables to be used by the Proposer as appropriate in relation to the Employers Requirement)]

Activity 3: Construction-Civil Works

| Sub-activity No. | Description of Sub-activity | Sub-activity Price |
| --- | --- | --- |
| 3.1 | Water Retaining Structures (e.g. Pre Treatment, Biological Treatment, Tertiary Treatment, Sludge Treatment, Sewage Diversion from Phase 1 area, Emergency outfall etc) (Bidder shall expand this to suit the suggested treatment process). |  |
| 3.2 | Water Retaining Structures after Hydraulic Testing |  |
| 3.3 | Water Retaining Structures after successful completion of testing, trial run, and performance guarantee test |  |
| 3.4 | Non Water Retaining Structures (Like Pump House, In Vessel Composting Plant building, Electrical Panel Room Blower Room, Admin Building, Laboratory, Roads, Drains Pathways, Landscaping& Tree planting, etc). ) (Bidder shall expand this to suit) |  |
| 3.5 | Non Water Retaining Structures On completion of work & putting the plant/unit in to full service. |  |
|  | ----------(Bidders to add as required) |  |
|  | Total price of Sub-activities carried forward to the Priced Activity Schedule, Page ____ |  |
|  | Total price of Sub-activities in words carried forward to the Priced Activity Schedule, Page ____ |  |

Part [1] Proposal Price Forms - Design-Build

Sample Schedule of Priced Sub- activities Table

[To be completed by the Proposer (more tables to be used by the Proposer as appropriate in relation to the Employers Requirement)]

4: Mechanical & Electrical. Instrumentation  Plant and Equipment for Incorporation in the Permanent Works ( including trial run )

| Sub-activity No. | Description of Sub-activity | Sub Activity Price |
| --- | --- | --- |
| 4.1 | M&E and ancillary equipment required for incorporation in the Permanent works. Procure and Supply all Mechanical and Electrical Equipment including those required for sewage treatment, odour control and in vessel composting, Instrumentation, etc required for the Works. |  |
| 4.2 | Completion of installation: Installation of all the M&E and ancillary equipment on site. |  |
| 4.3 | Completion of Testing: Successful completion of testing, trial run, commissioning and performance guarantee test |  |
| 4.4 | ----------(Bidders to add as required) |  |
|  | Total price of Sub-activities carried forward to the Priced Activity Schedule, Page ____ |  |
|  | Total price of Sub-activities in words carried forward to the Priced Activity Schedule, Page ____ |  |

Part [1] Proposal Price Forms - Design-Build

Specified Provisional Sums

| Item no. | Description | Amount |
| --- | --- | --- |
| 1 |  |  |
| 2 |  |  |
| 3 |  |  |
| 4 |  |  |
|  | Total for Specified Provisional Sums (carried forward to Grand Summary (B), p. ) |  |

Part [1] Proposal Price Forms - Design-Build

Summary (Design-Build)

| General Summary | Page | Amount |
| --- | --- | --- |
| Subtotal of Activities | (A) |  |
| Specified Provisional Sums ii | (B) | [sum] |
| Total of Activities and Provisional Sums (A + B +) i | (C) |  |
| Add Provisional Sum for Contingency Allowance (if any) ii | (D) | [sum] |
| Proposal Design Build Price (C + D) (Carried forward to Letter of Proposal) | (E) |  |
| i) All Provisional Sums are to be expended in whole or in part at the direction and discretion of the Employer’s Representative in accordance with Sub-Clause 13.5 of the General Conditions. except with respect to DAB Fees and Expenses for which Sub-Clause 13.5 of the Particular Conditions – Part B shall apply. ii) To be entered by the Employer. * For evaluation purposes, Provisional Sum will be excluded |  |  |

Part [2] Proposal Price Forms – Operation Service

Operation Service Fees (excl. Asset Replacement Fund)

| Ref. | Breakdown by Operation Service fees by revenue component | Totals | Yr. 1 | Yr. 2 | Yr. 3 | etc. |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A | e.g. Operation Service fixed fee |  |  |  |  |  |  |  |
| B | e.g. Operation Service variable fee |  |  |  |  |  |  |  |
| C | Totals |  |  |  |  |  |  |  |

i) 	All Provisional Sums are to be expended in whole or in part at the direction and discretion of the Employer’s Representative in accordance with Clause 13.5 of the Conditions of Contract.

ii) 	For evaluation purposes, Provisional Sums will be excluded

[The Employer shall adapt the form, and add additional forms, to suit the proposed Operation Service payment basis and permitted payment currencies. Add one additional Proposal form for each component of the Operation Service Fee]

Part [2] Proposal Price Forms – Operation Service

Asset Replacement Schedule

| Ref. | Asset description | Scheduled Replacement Date | Amount in currency of Proposal | % Local (q)* [state currency] | % FC1 (r)* [state currency] | % FC2 (s)* [state currency] | % FC# [state currency] |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Year 4 Asset Replacements |  |  |  |  |  |  |
|  | (a) Asset …. |  |  |  |  |  |  |
|  | (b) Asset …… |  |  |  |  |  |  |
|  | Total Year 4 Asset Replacements |  | …………. (Carried to Form 2a) |  |  |  |  |
| 2 | Year 8 Asset Replacements |  |  |  |  |  |  |
|  | (a) Asset …. |  |  |  |  |  |  |
|  | (b) Asset …… |  |  |  |  |  |  |
|  | Total Year 8 Asset Replacements |  | …………. (Carried to Form 2a) |  |  |  |  |
|  | Continue table for each year of the operation service |  |  |  |  |  |  |

* “q”, “r” and “s” etc. are the proportions in each currency to be used for cost indexation purposes as further detailed in Section IX, Contract Agreement, Appendix 2 – Schedule of Cost Indexation.

[The Employer shall adapt the form if Proposers are allowed to be paid in multiple currencies.]

Part [2] Proposal Price Forms – Operation Service

Summary for Operation Service

| Ref. | Activity | Total Operation Service Period [sum all years] | Yr. 1 | Yr. 2 | Yr. 3 | etc. |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A | Operation Service (excluding asset replacement fund) |  |  |  |  |  |  |  |
| B | Asset Replacement Fund (year 4 onwards) |  |  |  |  |  |  |  |
| C | Totals |  | Total carried forward |  |  |  |  |  |

Part 3: Grand Summary

| General Summary | Page | Amount |
| --- | --- | --- |
| 1. Proposal Design-Build Price |  | Sum |
| 2. Proposal Operation Service Price |  | Sum |
| 3. Proposal total price (Design-Build + Operation Service Price (Carried forward to Letter of Proposal) |  | Sum |

Technical Proposal Forms

Design Methodology	95

Construction Management Strategy	1-96

Design Build. Method Statements for key construction activities	1-97

Code of Conduct for Contractor’s Personnel (ES) Form	1-98

Design Build Work Program	1-102

Design Build Personnel Organization Chart	1-103

Operation Service Proposals	1-104

Form EQU. Contractor’s Equipment	1-105

Form PER -1. Contractor’s Representative and Key Proposed Personnel	1-106

Form PER-2. Resume and Declaration of Contractor’s Representative and Key Personnel	1-108

Risk assessment	1-110

Proposed Subcontractors for Major Activities/Sub-Activities	1-111

Qualification Forms	1-112

Form ELI 1.1. Proposer Information Sheet	1-113

Form ELI 1.2.  Party to JV Information Sheet	1-115

Form CON – 2.  Historical Contract Non-Performance, and Pending Litigation	1-116

Form CON – 3. Environmental and Social Performance Declaration	1-118

Form CCC Current Contract Commitments / Works in Progress	1-120

Form FIN – 3.1: Financial Situation and Performance	1-121

Form FIN - 3.2: Average Annual Construction Turnover	1-123

Form FIN 3.3. Financial Resources	1-124

Form EXP - 4.1: Specific DBO Experience	1-125

Form EXP - 4.2: Specific Design Experience	1-127

Form EXP - 4.3: Specific Construction Experience	1-129

Form EXP - 4.4: Specific Operations Experience	1-131

Form EXP - 4.5 : Specific Experience in Managing ES aspects	1-133

Others	1-134

Form of Proposal Security – Demand Guarantee	1-135

Form of Proposal-Securing Declaration	1-137

FORM OF POWER OF ATTORNEY FOR JOINT VENTURE	1-138

Design Methodology

## The Proposer shall submit a design methodology which addresses as a minimum the following:

- organizational arrangements for the design including team structure, roles and responsibilities, interface arrangements, design review and approval procedures and quality assurance arrangements;

- Proposed design deliverables: As per Employers requirements;

- Tender design deliverables to be included in the Proposal are detailed process and hydraulic calculation with necessary drawings such as layout of STP, P&ID and single line diagram.

- design statement setting out how the Employers Requirements will be achieved;

- Any added value the Proposer will bring including examples of innovative aspects of the design;

- comments on the Employer's Requirements, including:

- status of the information available and relevant design issues for the Works;

- comments on any errors, defects or ambiguities noted in the Employer’s Requirements; and

- Sustainable Procurement: sustainability aspects (e.g. energy efficiency, reduction of wastages, material reduction, sources of materials etc.) demonstrating the Proposer’s approach and commitment to sustainable design and construction practices;

- strategy for gathering baseline ES information in time to inform design development;

- details of how the ES requirements and any proposal to enhance ES outcomes will be incorporated into all design stages and how the implications for the construction phase has been considered;

- details of the approach to managing risks, stakeholder engagement, consultation and environmental permits/consents;

- value engineering (value management) arrangements, including consideration of ES issues; and

Construction Management Strategy

The Proposer shall submit a construction management strategy which addresses as a minimum:

        - organizational arrangements for the construction management including: team structure, roles and responsibilities, interface arrangements, approval procedures and quality assurance arrangements;

        - subcontractor selection and management;

        - proposals for training all personnel attending site;

        - stakeholder engagement;

        - obtaining and managing consents, permits and approvals;

        - site setup proposals including access, accommodation, welfare facilities, arrangement for plant and material storage;

        - construction phasing proposals including sequence of work and management of conflicting activities;

        - ensuring that geotechnical investigations or other advance works meet the ES requirements;

        - risk management approach for geotechnical and subsurface aspects of the Works;

        - quality management system including a draft of the quality management plan;

        - sustainability aspects demonstrating the Proposer’s approach and commitment to sustainable construction practices (e.g. energy efficiency, reduction of wastages, material reduction and sources of materials etc.);

        - preparation, approval and implementation of the Contractor’s environmental and social management plan;

        - preparation, approval and implementation of the Contractor’s health and safety manual;

        - grievance redress mechanisms;

        - reporting arrangements, including topics (that include ES) and timescales in accordance with the Particular Conditions Special Provisions  Sub-Clause 4.21;

        - arrangements for testing upon completion of the works;

        - arrangements for site handover, including completion of as-built drawings, preparation of operation and maintenance manuals, and any other relevant aspects; and

Design Build.
Method Statements for key construction activities

The Proposer shall provide its method statements for addressing the following risks and  carrying out the following construction activities. Each method statement shall describe the proposed approach, the level of staffing and experience, the safe system of work, and the equipment or materials to be used to manage risk or activity in accordance with the Employer’s Requirements.

ES Management Strategies and Implementation Plans

#### The Proposer shall submit Environmental and Social Management Strategies and Implementation Plans (ES-MSIP) as required by ITB 12.2 (k) of the Proposal Data Sheet.

#### In developing these strategies and plans, the Proposer shall have regard to the ES provisions of the contract including those as may be more fully described in the Employer’s Requirements in Section VII.

Code of Conduct for Contractor’s Personnel (ES) Form

Note to the Proposer:

The minimum content of the Code of Conduct form as set out by the Employer shall not be substantially modified. However, the Proposer may add requirements as appropriate, including to take into account Contract-specific issues/risks.

The Proposer shall initial and submit the Code of Conduct form as part of its proposal.

CODE OF CONDUCT FOR CONTRACTOR’S PERSONNEL

We are the Contractor, [enter name of Contractor].  We have signed a contract with [enter name of Employer] for [enter description of the Works]. These Works will be carried out at [enter the Site and other locations where the Works will be carried out]. Our contract requires us to implement measures to address environmental and social risks related to the Works, including the risks of sexual exploitation, sexual abuse and sexual harassment.

This Code of Conduct is part of our measures to deal with environmental and social risks related to the Works. It applies to all our staff, labourers and other employees at the Works Site or other places where the Works are being carried out.  It also applies to the personnel of each subcontractor and any other personnel assisting us in the execution of the Works.  All such persons are referred to as “Contractor’s Personnel” and are subject to this Code of Conduct.

This Code of Conduct identifies the behavior that we require from all Contractor’s Personnel.

Our workplace is an environment where unsafe, offensive, abusive, or violent behavior will not be tolerated and where all persons should feel comfortable raising issues or concerns without fear of retaliation.

REQUIRED CONDUCT

Contractor’s Personnel shall:

- carry out his/her duties competently and diligently;

- comply with this Code of Conduct and all applicable laws, regulations and other requirements, including requirements to protect the health, safety and well-being of other Contractor’s Personnel and any other person;

- maintain a safe working environment including by:

  - ensuring that workplaces, machinery, equipment and processes under each person’s control are safe and without risk to health;

  - wearing required personal protective equipment;

  - using appropriate measures relating to chemical, physical and biological substances and agents; and

  - following applicable emergency operating procedures.

- report work situations that he/she believes are not safe or healthy and remove himself/herself from a work situation which he/she reasonably believes presents an imminent and serious danger to his/her life or health;

- treat other people with respect, and not discriminate against specific groups such as women, people with disabilities, migrant workers or children;

- not engage in any form of Sexual Harassment, which means unwelcome sexual advances, requests for sexual favors, and other verbal or physical conduct of a sexual nature with other Contractor’s or Employer’s Personnel;

- not engage in Sexual Exploitation, which means any actual or attempted abuse of position of vulnerability, differential power or trust, for sexual purposes, including, but not limited to, profiting monetarily, socially or politically from the sexual exploitation of another;

- not engage in Sexual Abuse, which means the actual or threatened physical intrusion of a sexual nature, whether by force or under unequal or coercive conditions;

- not engage in any form of sexual activity with individuals under the age of 18, except in case of pre-existing marriage;

- complete relevant training courses that will be provided related to the environmental and social aspects of the Contract, including on health and safety matters, Sexual Exploitation and Abuse (SEA), and Sexual Harassment (SH);

- report violations of this Code of Conduct; and

- not retaliate against any person who reports violations of this Code of Conduct, whether to us or the Employer, or who makes use of the grievance mechanism for Contractor’s Personnel or the project’s Grievance Redress Mechanism.

RAISING CONCERNS

If any person observes behavior that he/she believes may represent a violation of this Code of Conduct, or that otherwise concerns him/her, he/she should raise the issue promptly. This can be done in either of the following ways:

- Contact [enter name of the Contractor’s Social Expert with relevant experience in handling sexual exploitation, sexual abuse and sexual harassment cases, or if such person is not required under the Contract, another individual designated by the Contractor to handle these matters] in writing at this address [   ] or by telephone at [   ] or in person at [   ]; or

- Call [  ]  to reach the Contractor’s hotline (if any) and leave a message.

The person’s identity will be kept confidential, unless reporting of allegations is mandated by the country law. Anonymous complaints or allegations may also be submitted and will be given all due and appropriate consideration. We take seriously all reports of possible misconduct and will investigate and take appropriate action. We will provide warm referrals to service providers that may help support the person who experienced the alleged incident, as appropriate.

There will be no retaliation against any person who raises a concern in good faith about any behavior prohibited by this Code of Conduct.  Such retaliation would be a violation of this Code of Conduct.

CONSEQUENCES OF VIOLATING THE CODE OF CONDUCT

Any violation of this Code of Conduct by Contractor’s Personnel may result in serious consequences, up to and including termination and possible referral to legal authorities.

FOR CONTRACTOR’S PERSONNEL:

I have received a copy of this Code of Conduct written in a language that I comprehend.  I understand that if I have any questions about this Code of Conduct, I can contact [enter name of Contractor’s contact person with relevant experience] requesting an explanation.

Name of Contractor’s Personnel: [insert name]

Signature: __________________________________________________________

Date: (day month year): _______________________________________________

Countersignature of authorized representative of the Contractor:

Signature: ________________________________________________________

Date: (day month year): _____________________________________________

ATTACHMENT 1: Behaviors constituting Sexual Exploitation and Abuse (SEA) and behaviors and behaviors constituting Sexual Harassment (SH)

ATTACHMENT 1 TO THE CODE OF CONDUCT FORM

BEHAVIORS CONSTITUTING SEXUAL EXPLOITATION AND ABUSE (SEA) AND BEHAVIORS CONSTITUTING SEXUAL HARASSMENT (SH)

The following non-exhaustive list is intended to illustrate types of prohibited behaviors.

- Examples of sexual exploitation and abuse include, but are not limited to:

- A Contractor’s Personnel tells a member of the community that he/she can get them jobs related to the work site (e.g. cooking and cleaning) in exchange for sex.

- A Contractor’s Personnel that is connecting electricity input to households says that he can connect women headed households to the grid in exchange for sex.

- A Contractor’s Personnel rapes, or otherwise sexually assaults a member of the community.

- A Contractor’s Personnel denies a person access to the Site unless he/she performs a sexual favor.

- A Contractor’s Personnel tells a person applying for employment under the Contract that he/she will only hire him/her if he/she has sex with him/her.

- Examples of sexual harassment in a work context

- Contractor’s Personnel comment on the appearance of another Contractor’s Personnel (either positive or negative) and sexual desirability.

- When a Contractor’s Personnel complains about comments made by another Contractor’s Personnel on his/her appearance, the other Contractor’s Personnel comment that he/she is “asking for it” because of how he/she dresses.

- Unwelcome touching of a Contractor’s or Employer’s Personnel by another Contractor’s Personnel.

- A Contractor’s Personnel tells another Contractor’s Personnel that he/she will get him/her a salary raise, or promotion if he/she sends him/her naked photographs of himself/herself.

Design Build Work Program

The Proposer shall set out a work program for design and construction of the Works to be undertaken, including identification of major milestones and critical path. The proposed work program shall be developed based on the Employer’s Requirements and shall consider the following key milestones:

- design of the Works, including the submission of the design deliverables, review and approval of the design by the Employer’s Representative

- processes and deliverables needed to commence the Works;

- execution of the Works within the Time for Completion, highlighting activities imposing constraints on the construction sequence;

- testing, commissioning and handing over of the completed Works;

- No-objection to the Contractor’s MSIPs, which collectively form the C-ESMP, in accordance with the Particular Conditions of Contract Sub-Clause 4.1;

- Constitution of the DAB; and

Design Build Personnel Organization Chart

The Proposer shall provide an organization chart illustrating the proposed management structure and reporting lines for delivery of the Design Build. The organization chart shall include the names of all Key Personnel.

Operation Service Proposals

The Proposer shall set out a detailed plan for the Operation Service which shall address the following:

- Organisation and key personnel

- Operations proposals

- Preventative and reactive maintenance

- Monitoring water/wastewater quality and flows

- The operational systems to be developed, including details of any standards to be adopted or followed for example with respect to managing environmental and social risks during operation

- Training of Contractor’s Personnel

- Asset replacement

- Preparation of required documents and manuals

- Quality assurance

- Hand-back arrangements

- Emergency Preparedness and Response Plan

- Reporting arrangements, including the appropriate topics (that include ES) and timescales in accordance with the Particular Conditions of Contract Sub-Clause 4.21

Form EQU.
Contractor’s Equipment

The Proposer shall set out its strategy for obtaining or accessing the key equipment necessary to execute the Works in accordance with the Design Build Works Program. In the strategy, the Proposer shall specify the manufacturer, capacity, model, power rating, age and maintenance condition, and how it will ensure that the equipment is maintained in accordance with manufacturer’s specifications for the duration of the Contract. The Proposer shall specify whether it will own, lease, rent or specially manufacture the key equipment.

A separate Form shall be prepared for each item of equipment listed, or for alternative equipment proposed by the Proposer.

| Item of equipment |  |  |
| --- | --- | --- |
| Equipment information | Name of manufacturer | Model and power rating |
|  | Capacity | Year of manufacture |
| Current status | Current location |  |
|  | Details of current commitments |  |
| Source | Indicate source of the equipment o Owned o Rented o Leased o Specially manufactured |  |

Omit the following information for equipment owned by the Proposer.

| Owner | Name of owner |  |
| --- | --- | --- |
|  | Address of owner |  |
|  | Telephone | Contact name and title |
|  | Fax | Telex |
| Agreements | Details of rental / lease / manufacture agreements specific to the project |  |

Form PER -1.
Contractor’s Representative and Key Proposed Personnel

Proposers should provide the names and details of suitably qualified Contractor’s Representative and Key Personnel to perform the Contract. The data on their experience should be supplied using the Form PER-2 below for each candidate. Proposers should submit a fully detailed Key Personnel resource schedule for the whole contract implementation period. The resource schedule must include:

- the name and role for each Key Personnel position

- The duration of each Key Personnel appointment

- The level of effort (time) allocated to each Key Personnel position and its distribution throughout the contract implementation period.

|  | Title of position | Name of candidate |  |  |
| --- | --- | --- | --- | --- |
| 1 | [Contractor’s Representative] |  |  |  |
| Key Personnel for Design |  |  |  |  |
| 2. | [Design Manager] |  |  |  |
| 3. | [Process designer] |  |  |  |
| 4. | [Social Impact Assessment Specialist] |  |  |  |
| 5. | Safety, Health and Environment Officer |  |  |  |
| 6. | [Modify/add others as appropriate] |  |  |  |
| Key Personnel for Construction |  |  |  |  |
| 7. | [Construction Manager] |  |  |  |
| 8. | [Environmental Specialist] |  |  |  |
| 9. | [Health and Safety Specialist] |  |  |  |
| 10. | [Social Specialist] |  |  |  |
| 11. | Survey Manager |  |  |  |
| 12. | [Sexual Exploitation, Abuse and Harassment Expert(s) [Where a Project SEA risks are assessed to be substantial or high, Key Personnel shall include an expert (s) with relevant experience in addressing sexual exploitation, sexual abuse and sexual harassment cases] |  |  |  |
| 13 | [Quality Assurance Manager] |  |  |  |
| 14. | [Modify/add others as appropriate] |  |  |  |
| Key Personnel for operation service |  |  |  |  |
| 15. | Plant Manager |  |  |  |
| 16. | EHS Manager |  |  |  |
| 17. | Community Relations Manager |  |  |  |
| 18. | [Accident prevention Officer] |  |  |  |
| 19. | [Process control engineer] |  |  |  |
| 20. | [Modify/add others as appropriate] |  |  |  |

Form PER-2.
Resume and Declaration of Contractor’s Representative and Key Personnel

Name of Proposer

| Position (title of position from Forms PER-1) |  |  |
| --- | --- | --- |
| Personnel information | Name | Date of birth |
|  | Address | Email |
|  | Professional qualifications |  |
|  | Academic qualifications |  |
|  | Language proficiency [language and levels of speaking, reading and writing skills] |  |
| Present employment | Name of employer |  |
|  | Address of employer |  |
|  | Telephone | Contact (manager / personnel officer) |
|  | Fax | E-mail |
|  | Job title | Years with present employer |

Summarize professional experience over the last [20 years], in reverse chronological order. Indicate particular technical and managerial experience relevant to the project.

| From | To | Company / Project / Position / Relevant technical and management experience |
| --- | --- | --- |

Declaration

I, the undersigned Key Personnel, certify that to the best of my knowledge and belief, the information contained in this Form PER-2 correctly describes myself, my qualifications and my experience.

I confirm that I am available as certified in the following table and throughout the expected time schedule for this position as provided in the Proposal:

| Commitment | Details |
| --- | --- |
| Commitment to duration of contract: | [insert period (start and end dates) for which this Key Personnel is available to work on this contract] |
| Time commitment: | [insert the number of days/week/months/ that this Key Personnel will be engaged] |

I understand that any misrepresentation or omission in this Form may:

- be taken into consideration during Proposal evaluation;

- my disqualification from participating in the Proposal;

- my dismissal from the contract.

Name of Key Personnel: [insert name]

Signature:

Date: (day month year):

Countersignature of authorized representative of the Proposer:

Signature:

Date: (day month year):

Risk assessment

The Proposer should submit a risk register identifying the hazards anticipated during the implementation of the contract.

For the key hazards ranked by impact, the risk register shall include a description of the hazard, an assessment of the potential impact on health and safety, environment, cost, program or other, and the proposed mitigation strategy for each hazard.

Proposed Subcontractors for Major Activities/Sub-Activities (Not Applicable)

The following Subcontractors and/or manufacturers are proposed for carrying out the activity/sub-activity indicated. For any additional subcontractor (Proposers are free to propose more than one for each activity/sub-activity.

| Activity/Sub-Activity | Proposed Subcontractors | Nationality |
| --- | --- | --- |

Proposers shall submit an undertaking from each proposed subcontractor to confirm that they have read, understand and will comply with the ES obligations and code of conduct.

Form of Sub-Contractor ESHS Undertaking

(to be filled in by each proposed subcontractor)

Date: ________________

Proposal No.: ________________

Alternative No.: ________________

Contract title: [insert the name of the contract]

To: [insert the name of the Employer’s agency]

We, the undersigned, confirm that we have read, understand and will comply with the ESHS obligations and code of conduct for the above mentioned contract.

Name of the Proposed subcontractor:

Name and title of the person signing this undertaking on behalf of the subcontractor:

___________________________________________________________________

____________________________

Signature of the person named above

____________________________

Date signed

Name of the person duly authorized to sign the Proposal on behalf of the Proposer	_______

Title of the person signing the Proposal	______________________

Signature of the person named above	______________________

Date signed ________________________________ day of ___________________, _____

Qualification Forms

Form ELI 1.1.
Proposer Information Sheet

Date: ______________________

RFP No.: ___________________

Page ________ of _______ pages

1. Proposer’s Legal Name

2. In case of JV, legal name of each party:

3. If permitted under ITP 4.3, names of JV members that wish to form an SPV:

4. Proposer’s actual or intended Country of Registration:

5. Proposer’s Year of Registration:

6. Proposer’s Legal Address in Country of Registration:

7. Proposer’s Authorized Representative [Lead Member] Information Name: Address: Telephone/Fax numbers: Email Address:

8. Attached are copies of original documents of  Articles of Incorporation (or equivalent documents of constitution or association), and/or documents of registration of the legal entity named above, in accordance with ITP 4.4  In case of JV, letter of intent to form JV or JV agreement, in accordance with ITP 4.1  In case of state-owned enterprise or institution, in accordance with ITP 4.6, documents establishing: - Legal and financial autonomy - Operation under commercial law - Establishing that the Proposer is not under the supervision of the Employer 9. Included are the organizational chart, a list of Board of Directors, and the beneficial ownership. [If required under PDS ITP 53.1, the successful Proposer shall provide additional information on beneficial ownership, using the Beneficial Ownership Disclosure Form.]

Form ELI 1.2. 
Party to JV Information Sheet

[The following form is additional to Form ELI – 1.1., and shall be completed to provide information relating to each JV member (in case the Applicant is a JV) as well as any Subcontractor proposed to be used by the Applicant for any part of the Contract]

Date: ______________________

RFP No.: ___________________

Page ________ of _______ pages

1. Proposer’s Legal Name:

2. JV’s Party legal name:

3. JV’s Party Country of Registration:

4. JV’s Party Year of Registration:

5. JV’s Party Legal Address in Country of Registration:

6. JV’s Party Authorized Representative Information Name: Address: Telephone/Fax numbers: Email Address:

7. Attached are copies of original documents of  Articles of Incorporation (or equivalent documents of constitution or association), and/or registration documents of the legal entity named above, in accordance with ITP 4.4.  In case of a state-owned enterprise or institution, documents establishing legal and financial autonomy, operation in accordance with commercial law, and that they are not under the supervision of the Employer, in accordance with ITP 4.6. 8. Included are the organizational chart, a list of Board of Directors, and the beneficial ownership. [If required under PDS ITP 53.1, the successful Proposer shall provide additional information on beneficial ownership for each JV member using the Beneficial Ownership Disclosure Form.]

9. Does the JV wish to form an SPV [yes/ no] only relevant where PDS permits formation of SPV]

Form CON – 2. 
Historical Contract Non-Performance, and Pending Litigation

[The following table shall be filled in for the Proposer and for JVs, each member of the Joint Venture]

Proposer’s Name: ________________

Date: ______________________

JV Member’s Name_________________________

RFP No. and title: ___________________________

Page _______________of ______________pages

| Non-Performed Contracts in accordance with Section III, Evaluation and Qualification Criteria |  |  |  |
| --- | --- | --- | --- |
|  Contract non-performance did not occur since 1st January [insert year]  Contract(s) not performed since 1st January [insert year] |  |  |  |
| Year | Non- performed portion of contract | Contract Identification | Total Contract Amount (current value, currency, exchange rate and US$ equivalent) |
| [insert year] | [insert amount and percentage] | Contract Identification: [indicate complete contract name/ number, and any other identification] Name of Employer: [insert full name] Address of Employer: [insert street/city/country] Reason(s) for nonperformance: [indicate main reason(s)] | [insert amount] |
| Pending Litigation, in accordance with Section III, Evaluation and Qualification Criteria |  |  |  |
|  No pending litigation |  |  |  |
|  Pending litigation |  |  |  |

| Year of dispute | Amount in dispute (currency) | Contract Identification | Total Contract Amount (currency), USD Equivalent (exchange rate) |
| --- | --- | --- | --- |
|  |  | Contract Identification: Name of Employer: Address of Employer: Matter in dispute: Party who initiated the dispute: Status of dispute: |  |

Form CON – 3.
Environmental and Social Performance Declaration

[The following table shall be filled in for the Proposer and for JVs, each member of the Joint Venture and each Subcontractor]

Proposer’s Name: [insert full name]

Date: [insert day, month, year]

Joint Venture Member’s or Subcontractor’s Name: [insert full name]

RFP No. and title: [insert RFP number and title]

Page [insert page number] of [insert total number] pages

| Environmental and Social Performance Declaration in accordance with Section III, Qualification Criteria, and Requirements |  |  |  |
| --- | --- | --- | --- |
|  No suspension or termination of contract: An employer has not suspended or terminated a contract and/or called the performance security for a contract for reasons related to Environmental or Social (ES) performance since the date specified in Section III, Qualification Criteria, and Requirements, Sub-Factor 2.5.  Declaration of suspension or termination of contract: The following contract(s) has/have been suspended or terminated and/or Performance Security called by an employer(s) for reasons related to Environmental or Social (ES) performance since the date specified in Section III, Qualification Criteria, and Requirements, Sub-Factor 2.5. Details are described below: |  |  |  |
| Year | Suspended or terminated portion of contract | Contract Identification | Total Contract Amount (current value, currency, exchange rate and US$ equivalent) |
| [insert year] | [insert amount and percentage] | Contract Identification: [indicate complete contract name/ number, and any other identification] Name of Employer: [insert full name] Address of Employer: [insert street/city/country] Reason(s) for suspension or termination: [indicate main reason(s)] | [insert amount] |
| [insert year] | [insert amount and percentage] | Contract Identification: [indicate complete contract name/ number, and any other identification] Name of Employer: [insert full name] Address of Employer: [insert street/city/country] Reason(s) for suspension or termination: [indicate main reason(s) e.g. gender-based violence; sexual exploitation or sexual abuse breaches] | [insert amount] |
| … | … | [list all applicable contracts] | … |
| Performance Security called by an employer(s) for reasons related to ES performance |  |  |  |
| Year | Contract Identification |  | Total Contract Amount (current value, currency, exchange rate and US$ equivalent) |
| [insert year] | Contract Identification: [indicate complete contract name/ number, and any other identification] Name of Employer: [insert full name] Address of Employer: [insert street/city/country] Reason(s) for calling of performance security: [indicate main reason(s) e.g. gender-based violence; sexual exploitation or sexual abuse breaches] |  | [insert amount] |

Form CCC
Current Contract Commitments / Works in Progress

Proposers and each partner to a JV should provide information on their current commitments on all contracts that have been awarded, or for which a letter of intent or acceptance has been received, or for contracts approaching completion, but for which an unqualified, full completion certificate has yet to be issued.

| Name of contract | Employer, contact address/tel/fax | Value of outstanding work (current US$ equivalent) | Estimated completion date | Average monthly invoicing over last six months (US$/month) |
| --- | --- | --- | --- | --- |
| 1. |  |  |  |  |
| 2. |  |  |  |  |
| 3. |  |  |  |  |
| 4. |  |  |  |  |
| 5. |  |  |  |  |
| etc. |  |  |  |  |

Form FIN – 3.1: Financial Situation and Performance

[The following table shall be filled in for the Applicant and for each member of a Joint Venture]

Applicant’s Name: [insert full name]
Date: [insert day, month, year]
Joint Venture Member Name: [insert full name]
RFP No. and title: [insert RFP number and title]
Page [insert page number] of [insert total number] pages

1. Financial data

| Type of Financial information in (currency) | Historic information for previous _ [insert number] years, [insert in words] (amount in currency, currency, exchange rate*, USD equivalent) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Year 1 | Year 2 | Year 3 | Year4 | Year 5 |
| Statement of Financial Position (Information from Balance Sheet) |  |  |  |  |  |
| Total Asses (TA) |  |  |  |  |  |
| Total Liabilities (TL) |  |  |  |  |  |
| Total Equity/Net Worth (NW) |  |  |  |  |  |
| Curent Asses (CA) |  |  |  |  |  |
| Curent Labilités (CL) |  |  |  |  |  |
| Waring Capital (WC) |  |  |  |  |  |
| Information from Income Statement |  |  |  |  |  |
| Total Revenue (TR) |  |  |  |  |  |
| Profits Before Taxes (PBT) |  |  |  |  |  |
| Cash Flow Information |  |  |  |  |  |
| Cash Flow from Operating Activities |  |  |  |  |  |

* Refer ITA 14 for the exchange rate

2. Sources of Finance

[The following table shall be filled in for the Applicant and all parties combined in case of a Joint Venture]

Specify sources of finance to meet the cash flow requirements on contracts currently in progress and for future contract commitments.

| No. | Source of finance | Amount (US$ equivalent) |
| --- | --- | --- |
| 1 |  |  |
| 2 |  |  |
| 3 |  |  |

3. Financial documents

The Applicant and its parties shall provide copies of financial statements for [number] years pursuant Section III, Table 1 –Qualification Criteria, and Requirements Sub-factor 3.1. The financial statements shall:

(a) 	reflect the financial situation of the Applicant or in case of JV member, and not an affiliated entity (such as parent company or group member).

(b)	be independently audited or certified in accordance with local legislation.

(c)	be complete, including all notes to the financial statements.

(d)	correspond to accounting periods already completed and audited.

Attached are copies of financial statements  for the [number] years required above; and complying with the requirements

Form FIN - 3.2: Average Annual Construction Turnover

[The following table shall be filled in for the Applicant and for each member of a Joint Venture]

Applicant’s Name: [insert full name]
Date: [insert day, month, year]
Joint Venture Member Name: [insert full name]
RFP No. and title: [insert RFP number and title]
Page [insert page number] of [insert total number] pages

| Annual Construction Turnover Data |  |  |  |
| --- | --- | --- | --- |
| Year | Amount Currency | Exchange rate* | USD equivalent |
| [indicate calendar year] | [insert amount and indicate currency] |  |  |
|  |  | Average Annual Construction Turnover ** |  |

*    Refer ITA 14 for date and source of exchange rate.

** 	Total USD equivalent for all years divided by the total number of years. See Section III, Table 1 Qualification Criteria, and Requirements, 3.2.

Form FIN 3.3.
Financial Resources

Specify proposed sources of financing, such as liquid assets, unencumbered real assets, lines of credit, and other financial means, net of current commitments, available to meet the total construction cash flow demands of the subject contract or contracts as indicated in Section III, Evaluation and Qualification Criteria

| Source of financing | Amount (US$ equivalent) |
| --- | --- |
| 1. |  |
| 2. |  |
| 3. |  |
| 4. |  |

Form EXP - 4.1: Specific DBO Experience

(Table 1, 4.1 and Table 2)

[The following table shall be filled in for contracts performed by the Applicant, each member of a Joint Venture, and Sub-contractors]

Applicant’s Name: [insert full name]
Date: [insert day, month, year]
Joint Venture Member Name: [insert full name]
RFP No. and title: [insert RFP number and title]
Page [insert page number] of [insert total number] pages

| Similar Contract No. [insert number] of [insert number of similar contracts required] | Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Contract Identification | [insert contract name and number, if applicable] |  |  |  |  |  |
| Award date | [insert day, month, year, e.g., 15 June, 2014] |  |  |  |  |  |
| Design-Build Commissioning Date | [insert day, month, year, e.g., 15 June, 2015] |  |  |  |  |  |
| Operations period completion date (actual or expected) | [insert day, month, year, e.g. 03 October, 2030] |  |  |  |  |  |
| Role in Contract [check the appropriate box] | Prime Contractor |  | Member in JV |  | Management Contractor | Sub-contractor |
| Total Contract Amount | [insert total contract amount in local currency] |  |  | US$ [insert Exchange rate and total contract amount in US$ equivalent] * |  |  |
| If member in a JV or sub-contractor, specify share in value in total Contract amount and roles and responsibilities | [insert a percentage amount] | [insert total contract amount in local currency] |  | [insert exchange rate and total contract amount in US$ equivalent] * |  |  |
|  | [insert roles and responsibilities] |  |  |  |  |  |
| Description of the similarity in accordance with Section III Table 1, 4.2 |  |  |  |  |  |  |
| Physical size of required contracts items | [insert physical size of items] |  |  |  |  |  |
| Complexity | [insert description of complexity] |  |  |  |  |  |
| Methods/Technology | [insert specific aspects of the methods/technology involved in the contract] |  |  |  |  |  |
| Other Characteristics | [insert other characteristics as described in Section VII, Scope of Employer’s Requirements] |  |  |  |  |  |
| Employer's Name: | [insert full name] |  |  |  |  |  |
| Address: Telephone/fax number E-mail: | [indicate street / number / town or city / country] [insert telephone/fax numbers, including country and city area codes] [insert e-mail address, if available] |  |  |  |  |  |

* Refer ITA 14 for date and source of exchange rate.

Form EXP - 4.2: Specific Design Experience

(Table 1, 4.2 and Table 2)

[The following table shall be filled in for contracts performed by the Applicant, each member of a Joint Venture, and Sub-contractors]

Applicant’s Name: [insert full name]
Date: [insert day, month, year]
Joint Venture Member Name: [insert full name]
RFP No. and title: [insert RFP number and title]
Page [insert page number] of [insert total number] pages

| Similar Contract No. [insert number] of [insert number of similar contracts required] | Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Contract Identification | [insert contract name and number, if applicable] |  |  |  |  |  |
| Award date | [insert day, month, year, i.e., 15 June, 2015] |  |  |  |  |  |
| Completion date | [insert day, month, year, i.e., 03 October, 2017] |  |  |  |  |  |
| Role in Contract [check the appropriate boxes] | Lead design |  | Process design |  | Detailed design | Other |
| Total Contract Amount | [insert total contract amount in local currency] |  |  | US$ [insert Exchange rate and total contract amount in US$ equivalent] * |  |  |
| If member in a JV or sub-contractor, specify share in value in total Contract amount and roles and responsibilities | [insert a percentage amount] | [insert total contract amount in local currency] |  | [insert exchange rate and total contract amount in US$ equivalent] * |  |  |
|  | [insert roles and responsibilities] |  |  |  |  |  |
| Description of the similarity in accordance with Section III Table 1, 4.2 |  |  |  |  |  |  |
| Physical size of required contracts items | [insert physical size of items] |  |  |  |  |  |
| Complexity | [insert description of complexity] |  |  |  |  |  |
| Methods/Technology | [insert specific aspects of the methods/technology involved in the contract] |  |  |  |  |  |
| Other Characteristics | [insert other characteristics as described in Section VII, Scope of Employer’s Requirements] |  |  |  |  |  |
| Employer's Name: | [insert full name] |  |  |  |  |  |
| Address: Telephone/fax number E-mail: | [indicate street / number / town or city / country] [insert telephone/fax numbers, including country and city area codes] [insert e-mail address, if available] |  |  |  |  |  |

* Refer ITA 14 for date and source of exchange rate.

Form EXP - 4.3: Specific Construction Experience

(Table 1, 4.3 and Table 2)

[The following table shall be filled in for contracts performed by the Applicant, each member of a Joint Venture, and Sub-contractors]

Applicant’s Name: [insert full name]
Date: [insert day, month, year]
Joint Venture Member Name: [insert full name]
RFP No. and title: [insert RFP number and title]
Page [insert page number] of [insert total number] pages

| Similar Contract No. [insert number] of [insert number of similar contracts required] | Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Contract Identification | [insert contract name and number, if applicable] |  |  |  |  |  |
| Award date | [insert day, month, year, i.e., 15 June, 2015] |  |  |  |  |  |
| Completion date | [insert day, month, year, i.e., 03 October, 2017] |  |  |  |  |  |
| Role in Contract [check the appropriate box] | Prime Contractor |  | Member in JV |  | Management Contractor | Sub-contractor |
| Total Contract Amount | [insert total contract amount in local currency] |  |  | US$ [insert Exchange rate and total contract amount in US$ equivalent] * |  |  |
| If member in a JV or sub-contractor, specify share in value in total Contract amount and roles and responsibilities | [insert a percentage amount] | [insert total contract amount in local currency] |  | [insert exchange rate and total contract amount in US$ equivalent] * |  |  |
|  | [insert roles and responsibilities] |  |  |  |  |  |
| Description of the similarity in accordance with Section III Table 1, 4.2 |  |  |  |  |  |  |
| Physical size of required contracts items | [insert physical size of items] |  |  |  |  |  |
| Complexity | [insert description of complexity] |  |  |  |  |  |
| Methods/Technology | [insert specific aspects of the methods/technology involved in the contract] |  |  |  |  |  |
| Other Characteristics | [insert other characteristics as described in Section VII, Scope of Employer’s Requirements] |  |  |  |  |  |
| Employer's Name: | [insert full name] |  |  |  |  |  |
| Address: Telephone/fax number E-mail: | [indicate street / number / town or city / country] [insert telephone/fax numbers, including country and city area codes] [insert e-mail address, if available] |  |  |  |  |  |

* Refer ITA 14 for date and source of exchange rate.

Form EXP - 4.4: Specific Operations Experience

(Table 1, 4.1 and Table 2)

[The following table shall be filled in for contracts performed by the Applicant, each member of a Joint Venture, and Sub-contractors]

Applicant’s Name: [insert full name]
Date: [insert day, month, year]
Joint Venture Member Name: [insert full name]
RFP No. and title: [insert RFP number and title]
Page [insert page number] of [insert total number] pages

| Similar Contract No. [insert number] of [insert number of similar contracts required] | Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Contract Identification | [insert contract name and number, if applicable] |  |  |  |  |  |
| Award date | [insert day, month, year, i.e., 15 June, 2015] |  |  |  |  |  |
| Contract Completion date (actual/expected) | [insert day, month, year, i.e., 03 October, 2017] |  |  |  |  |  |
| Role in Contract [check the appropriate box] | Prime Contractor |  | Member in JV |  | Management Contractor | Sub-contractor |
| Total Contract Amount | [insert total contract amount in local currency] |  |  | US$ [insert Exchange rate and total contract amount in US$ equivalent] * |  |  |
| If member in a JV or sub-contractor, specify share in value in total Contract amount and roles and responsibilities | [insert a percentage amount] | [insert total contract amount in local currency] |  | [insert exchange rate and total contract amount in US$ equivalent] * |  |  |
|  | [insert roles and responsibilities] |  |  |  |  |  |
| Description of the similarity in accordance with Section III Table 1, 4.2 |  |  |  |  |  |  |
| Physical size of required contracts items | [insert physical size of items] |  |  |  |  |  |
| Complexity | [insert description of complexity] |  |  |  |  |  |
| Methods/Technology | [insert specific aspects of the methods/technology involved in the contract] |  |  |  |  |  |
| Other Characteristics | [insert other characteristics as described in Section VII, Scope of Employer’s Requirements] |  |  |  |  |  |
| Employer's Name: | [insert full name] |  |  |  |  |  |
| Address: Telephone/fax number E-mail: | [indicate street / number / town or city / country] [insert telephone/fax numbers, including country and city area codes] [insert e-mail address, if available] |  |  |  |  |  |

* Refer ITA 14 for date and source of exchange rate.

Form EXP - 4.5 : Specific Experience in Managing ES aspects

[The following table shall be filled in for contracts performed by the Proposer, and each member of a Joint Venture]

Proposer Name: ________________
Date: ___________________
Proposer JV Member Name: __________________
RFP No. and title: _____________________

Page __________________of ________________pages

      - Key Requirement no 1 in accordance with 4.5: ______________________

| Contract Identification |  |  |  |  |
| --- | --- | --- | --- | --- |
| Award date |  |  |  |  |
| Completion date |  |  |  |  |
| Role in Contract | Prime Contractor | Member in JV | Management Contractor | Subcontractor |
| Total Contract Amount |  |  | US$ |  |
| Details of relevant experience |  |  |  |  |

      - Key Requirement no 2 in accordance with 4.5: ______________________

Key Requirement no 3 in accordance with 4.5: ______________________

Others

Commercial or contractual aspects of the RFP documents that the Proposer would like to discuss with the Employer during clarifications.

Form of Proposal Security – Demand Guarantee

Beneficiary:

Request for Proposals No:

Date:

PROPOSAL GUARANTEE No.:

Guarantor:

We have been informed that __________________________ (hereinafter called “the Applicant”) has submitted or will submit to the Beneficiary its Proposal (hereinafter called “the Proposal”) for the execution of ________________ under Request for Proposals No. ___________ (“the RFP”).

Furthermore, we understand that, according to the Beneficiary’s conditions, Proposals must be supported by a Proposal guarantee.

At the request of the Applicant, we, as Guarantor, hereby irrevocably undertake to pay the Beneficiary any sum or sums not exceeding in total an amount of ___________ (____________) upon receipt by us of the Beneficiary’s complying demand, supported by the Beneficiary’s statement, whether in the demand itself or a separate signed document accompanying or identifying the demand, stating that either the Applicant:

(a) 	has withdrawn its Proposal prior to the Proposal validity expiry date set forth in the Applicant’s Letter of Proposal, or any extension thereto provided by the Applicant; or

(b) 	having been notified of the acceptance of its Proposal by the Beneficiary prior to the expiry date of the Proposal validity  or any extension thereto provided by the Applicant, (i) has failed to execute the contract agreement, or (ii) has failed to furnish the Performance Security and, if required, an Environmental and Social (ES) Performance Security, in accordance with the Instructions to Proposers (“ITP”) of the Beneficiary’s RFP document.

This guarantee will expire: (a) if the Applicant is the successful Proposer, upon our receipt of copies of the contract agreement signed by the Applicant and the Performance Security and, if required, an Environmental and Social (ES) Performance Security issued to the Beneficiary in relation to such contract agreement; or (b) if the Applicant is not the successful Proposer, upon the earlier of (i) our receipt of a copy of the Beneficiary’s notification to the Applicant of the results of the RFP process; or (ii) twenty-eight days after the expiry date of the Proposal validity.

Consequently, any demand for payment under this guarantee must be received by us at the office indicated above on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees (URDG) 2010 Revision, ICC Publication No. 758.

[signature(s)]

Form of Proposal-Securing Declaration

Date: ________________

Proposal No.: ________________

Alternative No.: ________________

To:

We, the undersigned, declare that:

We understand that, according to your conditions, Proposals must be supported by a Proposal-Securing Declaration.

We accept that we will automatically be suspended from being eligible for submitting proposals or bidding in any contract with the Employer for the period of time of ______________ starting on _________, if we are in breach of our obligation(s) under the Proposal conditions, because we:

(a) 	have withdrawn our Proposal prior to the expiry date of the Proposal validity specified in the Letter of Proposal or any extended date provided by us; or

(b) 	having been notified of the acceptance of our Proposal by the Employer prior to  the expiry date of the Proposal validity in the Letter of Proposal or any extended date provided by us, (i) fail or refuse to execute the Contract, if required, or (ii) fail or refuse to furnish the Performance Security and, if required, an Environmental and Social (ES) Performance Security, in accordance with the ITP 54.

We understand this Proposal-Securing Declaration shall expire if we are not the successful Proposer, upon the earlier of (i) our receipt of your notification to us of the name of the successful Proposer; or (ii) twenty-eight days after the expiry date of of the Proposal validity.

Name of the Proposer*

Name of the person duly authorized to sign the Proposal on behalf of the Proposer**	_______

Title of the person signing the Proposal	______________________

Signature of the person named above	______________________

Date signed ________________________________ day of ___________________, _____

*: In the case of the Proposal submitted by joint venture specify the name of the Joint Venture as Proposer

**: Person signing the Proposal shall have the power of attorney given by the Proposer attached to the Proposal

[Note: In case of a Joint Venture, the Proposal-Securing Declaration must be in the name of all members to the Joint Venture that submits the Proposal.]

FORM OF POWER OF ATTORNEY FOR JOINT VENTURE

(On Non-judicial Stamp Paper of Appropriate value, if required as per laws of the country of the bidder, to be purchased in the Name of Joint Venture)

KNOW ALL MEN BY THESE PRESENTS THAT WE, the Partners whose details are given hereunder ................................................................................. have formed a Joint Venture under the   laws of 	........................................... (*)/ intend to form a Joint Venture (*) 	[(*) delete whichever is not applicable] and	having our Registered Office(s)/Head Office(s) at............................................... (hereinafter called the 'Joint Venture' which expression shall unless repugnant to the context or meaning thereof, include 	its  	successors,	administrators	and assigns) acting through	M/s ....................................................... being the Partner in-charge do hereby constitute, nominate and appoint M/s........................................................ a Company incorporated under the laws of .........................................................  and having its Registered/Head Office at ........................................... as our duly constituted lawful Attorney (hereinafter called "Attorney" or "Authorized Representative" or "Partner In-charge") to exercise all or any of the powers for and on behalf of the Joint Venture in regard to  work for the  bids  for which have been invited by ……………………………….., ……………………….. (hereinafter called the ‘Owner’) to undertake the following acts:

i)     To sign and submit proposal and participate in the aforesaid Proposal Specification of the Owner on behalf of the "Joint Venture".

ii)      To negotiate with the Owner the terms and conditions for award of the Contract pursuant to the aforesaid Proposal and to sign the Contract with the Owner for and on behalf of the "Joint Venture".

iii)     To do any other act or submit any document related to the above.

iv)     To receive, accept and execute the Contract for and on behalf of the "Joint Venture".

For the above purpose, the person(s) authorized by the Partner In-charge shall be the person(s) authorized to act on behalf of the "Joint Venture" as per the Power of Attorney given to him/her/them by the Partner In-Charge,

It is clearly understood that all the partners of the joint venture shall be liable jointly and severally for the execution of the Contract in accordance with the Contract terms and the Partner In-charge (Lead Partner) shall ensure performance of the Contract(s) and if one or more Partner fail to perform their respective portions of the Contract(s), the same shall be deemed to be a default by all the Partners.

It is expressly understood that this Power of Attorney shall remain valid binding and irrevocable till completion of the Design Build as well as the Operations and Maintenance Period in terms of the Contract.

The  Joint  Venture  hereby  agrees  and  undertakes  to  ratify  and  confirm  all  the whatsoever the said Attorney/Authorized Representatives/Partner in-charge quotes in the bid, negotiates and signs the Contract with the Owner and/or proposes to act on behalf of the Joint Venture by virtue of this Power of Attorney and the same shall bind the Joint Venture as if done by itself.

IN WITNESS THEREOF the Partners Constituting the Joint Venture as aforesaid have executed these presents on this   ...........day of   .......................under the Common Seal(s) of their Companies.

For and on behalf of the

Partners of Joint Venture

The Common Seal of the above Partners of the Joint Venture:

The Common Seal has been affixed there unto in the presence of: WITNESS

1.       Signature......................................................

Name.......................................................... Designation........................................................... Occupation.................................................

2.        Signature.....................................................

Name.........................................................

Designation................................................................ Occupation..........................................................

FORM OF UNDERTAKING BY THE JOINT VENTURE PARTNERS

(On Non-Judicial Stamp Paper of Appropriate Value, if required as per laws of the country of the bidder, to be purchased in the Name of Joint Venture)

THIS JOINT DEED OF UNDERTAKING executed on this ..........day of .......Two

Thousand and ..................by ....... a company incorporated under the laws of   ............... and having its Registered Office at........................ (hereinafter called the "Party No.1.. which expression shall include its successors, executors and permitted assigns) and M/s ............... a company incorporated under the      laws of .................. and having its Registered Office at ............... (hereinafter called the "Party No.2" which expression shall include its successors, executors and permitted assigns) and M/s .......................... a Company incorporated under the laws of .................... and having its Registered Office at ................ (hereinafter called the "Party No.3" which expression shall include its successors, executors and permitted assigns) for the purpose of making a Proposal and entering into a contract [hereinafter called the "Contract" (in case of award) against the work to design and build Sewage Treatment Plant and all Appurtenant Structures and Allied Works, and O & M of Complete Works associated with ……………………………… (hereinafter called the "Owner").

WHEREAS the Party No.1, Party No.2 and Party No.3 have entered into an Agreement dated................

AND WHEREAS the Owner invited bids as per the above mentioned Specification to design and build Sewage Treatment Plant and all Appurtenant Structures and Allied Works, and O & M of Complete Works stipulated in the bidding documents.

AND WHEREAS ITB Section 3 Qualification Criteria forming part of the bidding documents, inter-alia, stipulate that an undertaking of two or more qualified partners, meeting the requirements of ‘Qualification Criteria of the Bidder', as applicable may bid, provided, the Joint Venture fulfills all other requirements under Clause 6 ‘Qualification of the Bidder’ and in such a case, the Letter of Proposal (Proposal Form) shall be signed by the Partner - In Charge so as to legally bind all the Partners of the Joint Venture, who will be jointly and severally liable to perform the Contract and all obligations hereunder.

The above clause further states that this Undertaking shall be attached to the Proposal and the Contract performance guarantee will be as per the format enclosed with the bidding document without any restrictions or liability for either party.

AND WHEREAS the Proposal is being submitted to the Owner vide proposal No........dated...... by Party No.1 based on this Undertaking between all the parties; under these presents and the Proposal in accordance with the requirements stated in Section 3  Qualification Criteria, has been signed by all the parties.

NOW THIS UNDERTAKING WITNESSETH AS UNDER:

In consideration of the above premises and agreements all the parties of this Deed of Undertaking do hereby declare and undertake:

- In requirement of the award of the Contract by the Owner to the Joint Venture Partners, we, the Parties do hereby undertake that   M/s......... the Party No.1, shall act as Lead Partner and further declare and confirm that we the parties to the Joint Venture shall jointly and severally be bound unto the Owner for the successful performance of the Contract and shall be fully responsible to design and build Sewage Treatment Plant and all Appurtenant Structures and Allied Works, and O & M of Complete Works in accordance with the Contract.

- In case of any breach or default of the said Contract by any of the parties to the Joint Venture, the parties do hereby undertake to be fully responsible for the successful performance of the Contract and to carry out all the obligations and responsibilities under the Contract in accordance with the requirements of the Contract.

- Further, if the Owner suffers any loss or damage on account of any breach in the Contract or any shortfall in the performance of the equipment in meeting the performances guaranteed as per the specification in terms of the Contract, the Party(s)  of  these  presents  undertake  to  promptly  make  good  such  loss  or damages caused to the Owner, on its demand without any demur. It shall not be necessary or obligatory for the Owner to proceed against Lead Partner to these presents before proceeding against or dealing with the other Party(s), the Owner can  proceed  against  any  of  the  parties  who  shall be  jointly  and severally liable for the performance and all other liabilities/obligations under the Contract to the Owner.

- The financial liability of the Parties of this Deed of Undertaking to the Owner, with  respect  to  any  of  the  claims  arising  out  of  the  performance  or  non­performance of the obligations set forth in this Deed of Undertaking, read in conjunction with the relevant conditions of the Contract shall, however not be limited in any way so as to restrict or limit the liabilities or obligations of any of the Parties of this Deed of Undertaking.

- It is expressly understood and agreed between the Parties to this Undertaking that the responsibilities and obligations of each of the Parties shall be delineated (to be suitably appended by the Parties along with this undertaking in its bid). It is further undertaken by the parties that the above sharing of responsibilities and obligations shall not in any way be a limitation of joint and several responsibilities of the Parties under the Contract.

- It  is  also  understood that  this  Undertaking is  provided  for  the  purposes  of undertaking joint and several liabilities of the partners to the Joint Venture for submission of the Proposal and performance of the Contract if awarded and that this Undertaking shall not be deemed to give rise to any additional liabilities or obligations, in any manner or any law, on any of the Parties to this Undertaking or on the Joint Venture, other than the express provisions of the Contract.

- This Undertaking shall be construed and interpreted in accordance with the provisions of the Contract.

- In  case  of   an  award   of  a  Contract,  we  the  parties   to  this   Deed of Undertaking  do  hereby   agree   that   we  shall   be  jointly  and  severally responsible for furnishing a Contract performance security from  a bank  in favour of the Owner in the currency/currencies of the Contract.

- It is further agreed that this Deed of Undertaking shall be irrevocable and shall form an integral part of the Proposal and shall continue to be enforceable till the Owner discharges the same or upon the completion of the Contract in accordance with its provisions, whichever is earlier. It shall be effective from the date first mentioned above for all purposes and intents.

IN WITNESS WHEREOF, the Parties to this Deed of Undertaking have through their authorized representatives executed these presents and affixed Common Seals of their companies, on the day, month and year first mentioned above.

| Common Seal of ............................ has been affixed in my/ our presence pursuant to Board of Director's Resolution dated ............... | For Lead Partner (Party No.-1) For and on behalf of M/s |
| --- | --- |
| Name ........................................ |  |
| Designation .................................. |  |
| Signature ..................................... | Signature of the authorized representative) |
|  | For Party No.-2 For and on behalf of M/s....................... |
| WITNESS: |  |
| I……………………………………. |  |
| II……………………………………. |  |

| Common Seal of ............................ has been affixed in my/ our presence pursuant to Board of Director's Resolution dated ............... | For Party No.-2 For and on behalf of M/s |
| --- | --- |
| Name ........................................ |  |
| Designation .................................. |  |
| Signature ..................................... | Signature of the authorized representative) |
| WITNESS: |  |
| I……………………………………. |  |
| II……………………………………. |  |

| Common Seal of ............................ has been affixed in my/ our presence pursuant to Board of Director's Resolution dated ............... | For Party No.-3 For and on behalf of M/s |
| --- | --- |
| Name ........................................ |  |
| Designation .................................. |  |
| Signature ..................................... | Signature of the authorized representative) |
| WITNESS: |  |
| I……………………………………. |  |
| II……………………………………. |  |

Section V – Eligible Countries

Eligibility for the Provision of Goods, Works and non-consulting Services in Bank-Financed Procurement

In reference to ITP 4.8 and ITP 5.1, for the information of the Proposers, at the present time firms, goods and services from the following countries are excluded from this RFP process:

Under ITP 4.8(a) and ITP 5.1: Refer to “https://www.worldbank.org/en/projects-operations/procurement/debarred-firms”

Under ITP 4.8(b) and ITP 5.1: Refer to “https://www.worldbank.org/en/projects-operations/procurement/debarred-firms”

Section VI – Fraud and Corruption

(Section VI shall not be modified)

- Purpose

  - The Bank’s Anti-Corruption Guidelines and this annex apply with respect to procurement under Bank Investment Project Financing operations.

- Requirements

- The Bank requires that Borrowers (including beneficiaries of Bank financing); bidders (applicants/ proposers), consultants, contractors and suppliers; any sub-contractors, sub-consultants, service providers or suppliers; any agents (whether declared or not); and any of their personnel, observe the highest standard of ethics during the procurement process, selection and contract execution of Bank-financed contracts, and refrain from Fraud and Corruption.

- To this end, the Bank:

- Defines, for the purposes of this provision, the terms set forth below as follows:

- “corrupt practice” is the offering, giving, receiving, or soliciting, directly or indirectly, of anything of value to influence improperly the actions of another party;

- “fraudulent practice” is any act or omission, including misrepresentation, that knowingly or recklessly misleads, or attempts to mislead, a party to obtain financial or other benefit or to avoid an obligation;

- “collusive practice” is an arrangement between two or more parties designed to achieve an improper purpose, including to influence improperly the actions of another party;

- “coercive practice” is impairing or harming, or threatening to impair or harm, directly or indirectly, any party or the property of the party to influence improperly the actions of a party;

- “obstructive practice” is:

- deliberately destroying, falsifying, altering, or concealing of evidence material to the investigation or making false statements to investigators in order to materially impede a Bank investigation into allegations of a corrupt, fraudulent, coercive, or collusive practice; and/or threatening, harassing, or intimidating any party to prevent it from disclosing its knowledge of matters relevant to the investigation or from pursuing the investigation; or

- acts intended to materially impede the exercise of the Bank’s inspection and audit rights provided for under paragraph 2.2 e. below.

- Rejects a proposal for award if the Bank determines that the firm or individual recommended for award, any of its personnel, or its agents, or its sub-consultants, sub-contractors, service providers, suppliers and/ or their employees, has, directly or indirectly, engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices in competing for the contract in question;

- In addition to the legal remedies set out in the relevant Legal Agreement, may take other appropriate actions, including declaring misprocurement, if the Bank determines at any time that representatives of the Borrower or of a recipient of any part of the proceeds of the loan engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices during the procurement process, selection and/or execution of the contract in question, without the Borrower having taken timely and appropriate action satisfactory to the Bank to address such practices when they occur, including by failing to inform the Bank in a timely manner at the time they knew of the practices;

- Pursuant to the Bank’s Anti-Corruption Guidelines, and in accordance with the Bank’s prevailing sanctions policies and procedures, may sanction a firm or individual, either indefinitely or for a stated period of time, including by publicly declaring such firm or individual ineligible (i) to be awarded or otherwise benefit from a Bank-financed contract, financially or in any other manner; (ii) to be a nominated sub-contractor, consultant, manufacturer or supplier, or service provider of an otherwise eligible firm being awarded a Bank-financed contract; and (iii) to receive the proceeds of any loan made by the Bank or otherwise to participate further in the preparation or implementation of any Bank-financed project;

- Requires that a clause be included in bidding/request for proposals documents and in contracts financed by a Bank loan, requiring (i) bidders (applicants/ proposers), consultants, contractors, and suppliers, and their sub-contractors, sub-consultants, service providers, suppliers, agents personnel, permit the Bank to inspect all accounts, records and other documents relating to the procurement process, selection and/ or contract execution, and to have them audited by auditors appointed by the Bank.

PART 2 – Employer’s Requirements

Table of contents

1.	Summary of Employer’s Requirements	86

1.1.	The Project	86

1.2.	The Schedule of Performance Standards	86

1.2.1.	Performance Requirement of STP	86

1.2.2.	In-Vessel Sludge Composting Plant	88

1.2.3.	Ancillary and Other Works	91

1.3.	Limitations on process selection and design	91

1.4.	Nominated Sub-contractors and co-operation with other contractors	92

2.	The Site	93

2.1.	Description of Site and Site Access	93

2.2.	Right of Access to the Site	94

3.	STP Technical Requirements	95

3.1.	Description of Catchment	95

3.1.1.	Geographic area served by the STP	95

3.2.	Capacity of Sewage Treatment Plant	95

3.2.1.	Sewer network and Sea outfalls in Phase 1 area	95

3.2.2.	Diversion of sewage from Phase 1 area to STP	95

3.2.3.	Capacity of Sewage Treatment Plant	96

3.3.	Wastewater composition	96

3.3.1.	Base data on wastewater influent characteristics	96

3.4.	Effluent discharge requirements	97

3.5.	Sludge treatment and disposal requirements	98

3.5.1.	The Objectives	98

3.5.2.	Quality of Sludge	98

3.5.3.	In-Vessel composting sludge	98

3.5.4.	In-Vessel Sludge Composting Plant	99

3.5.5.	Composition of Compost Material	99

3.5.6.	Availability of Feed Material, Amendment and Bulker in Hulhumale for In-Vessel Composting (Indicative only)	99

3.5.7.	Design Criteria 	100

3.5.8.	Indicative design guide	100

3.6.	Efficiency requirements	101

3.7.	Other environmental requirements	101

3.7.1.	Odour Control	101

3.7.2.	Noise Nuisance 	102

3.8.	Materials requirements	102

3.8.1.	Acceptable Materials	102

3.8.2.	Reinforcement Cover	103

3.9.	Electricity and Power	104

3.9.1.	Available electrical supply to the STP	104

3.9.2.	Standby generation requirements	104

3.9.3.	On-site power generation	104

3.10.	Monitoring, sampling and testing equipment	105

3.10.1.	Flow parameters	105

3.10.2.	Sampling and testing equipment	105

3.10.3.	Site laboratory and equipment	110

3.11.	Other design-build requirement	110

3.11.1.	Site Access	110

3.11.2.	Instrumentation, SCADA and telemetry	110

3.11.3.	Septage receiving point	112

3.11.4.	Administration buildings, stores, workshops	112

3.11.5.	Security and boundary fencing	119

3.11.6.	Utilities, drainage, firefighting	120

3.11.8.	Diversion of Influent Sewer	121

3.11.7.Suggested Ancillary STP units and Requirements	121

4.	Planning, design, approvals and documents	140

4.1.	General	140

4.2.	The Environmental Management Plan	140

4.3.	Permits and approvals (requirements)	140

4.4.	Initial site investigations and studies	141

4.5.	Durability of the Works	141

4.6.	Contractors Documents (Design Build) and progress reports	142

4.6.1.	Submission and approval of Contractor’s Documents (Design-build)	142

4.6.2.	Design-Build Publications to be kept on Site	143

4.6.3.	Progress Reports during the Design-Build	143

5.	Existing Facilities	144

5.1.	Description of the Existing Facilities	144

5.2.	Contractor’s Responsibilities for rehabilitation of the Existing Facilities	144

5.3.	Contractor’s Responsibilities for operating the Existing Facilities	144

5.4.	Employer’s Equipment and free issue materials (Existing Facilities)	144

5.5.	Incorporation of Existing Facilities into the Works	145

6.	Demolition, earthworks, construction and commissioning	146

6.1.	General obligations	146

6.2.	Facilities for the Employer’s Personnel during the design build period	146

6.3.	Contractor’s site access and facilities	146

6.4.	Electricity, Water and Gas during the Design-Build	146

6.5.	Employer’s Equipment and free issue items (Design-Build)	147

6.6.	Demolition	147

6.7.	Samples and testing	147

6.8.	Payment of Royalties	147

6.9.	Tests on Completion of the Design-Build	147

6.9.1.	General	147

6.9.2.	Dry Test Requirements	150

6.9.3.	Safety Audit	152

6.9.4.	Process Wet Tests (with Raw Sewage)	153

6.9.5.	Effluent Quality Criteria for Passing the Tests on Completion	154

6.9.6.	Tests after Completion	154

6.9.7.	Criteria for Passing the Test after Completion	156

6.9.8.	Performance Certificate	156

7.	Operation Management Requirements	158

7.1.	General Requirements	158

7.1.1.	Overall description of the Operation Service	158

7.1.2.	Performance during the Operation Service Period	158

7.1.3.	Employer’s Equipment and free issue materials (Operation Service)	159

7.2.	Contractor’s Documents (Operation Service)	159

7.2.1.	General Requirements for Contractors Documents (Operation Service)	159

7.2.2.	Submission and approval of Contractor’s Documents (Operation Service)	160

7.2.3.	Operation Service Publications to be kept on Site	161

7.2.4.	Operating and Maintenance Manuals	161

7.2.5.	Emergency Response Plan	161

7.2.6.	Wastewater Quality Testing Plan	162

7.2.7.	Health and Safety Manual (Operation Service)	163

7.2.8.	Quality Assurance Manual	163

7.3.	Staff organisation and training	163

7.3.1.	Staff organisation	163

7.3.2.	Training of Contractor’s Personnel	164

7.3.3.	Training of Employer’s Personnel	164

7.4.	Health and safety	164

7.5.	Treatment and disposal of wastes from treatment operations	165

7.6.	Maintenance requirements	165

7.6.1.	General maintenance provisions	165

7.6.2.	Maintenance management system and inventory control	165

7.7.	Measurement and testing during the Operation Service Period	166

7.7.1.	General	166

7.7.2.	Flow measurement	166

7.7.3.	Sampling methods and frequencies	166

7.7.4.	Measurement of smell and noise	166

7.7.5.	Third party validation of results	167

7.8.	Asset Replacement	167

7.9.	Reporting requirements during the Operation Service Period	167

7.9.1.	Information to be notified immediately	167

7.9.2.	Monthly progress report	167

7.9.3.	Annual report	168

7.9.4.	Documents to be held on site during the Operation Service Period	168

8.	Contractor’s Staff and expertise	169

8.1.	General	169

9.	Hand-Back Requirements	172

9.1.	General requirements	172

9.2.	Hand-back inventories	172

9.3.	Training of Employer’s follow-on O&M personnel	173

10.	Terms of appointment for the Auditing Body	174

10.1.	General	174

10.2.	The procedure for appointment of the Auditing Body	174

10.3.	Reappointment procedure	174

10.4.	Scope of services of the Auditing Body	174

11.	Standards and codes	176

Appendix 1: Environmental Management Plan	180

Appendix 2: Financial Memorandum	182

# 1.	Summary of Employer’s Requirements

  - The Project

The Project comprises the design, construction, supply, testing, commissioning, and operation and maintenance for 10 years of the 10 mld Sewage Treatment Plant (STP) at Hulhumalé, including diversion of raw sewage from the pumping mains/pumping stations, that discharges sewage to outfall 1 and 2, to the inlet works of the STP. In addition to the above, the project includes design, procurement, installation and commissioning of In Vessel Sludge Composting Plant for treatment of sludge produced at the STP and Installation and commissioning of Odour Control System for the STP.

## 1.2.	The Schedule of Performance Standards and Indicative Design Data

The Contractor shall plan, design, construct, operate and maintain the Works as necessary to meet the standards specified in the Schedule of Performance Standards. In the case of any conflict between the standards specified in the Employer’s Requirements and those specified in the Schedule of Performance Standards, the requirements of the Schedule of Performance Standards will take precedence.

1.2.1	Performance Requirement of STP

- Selection of Treatment Process

The Contractor is free to select any treatment technology which has proven track record to meet all the requirements of the Employer specified in the DBO Contract documents.  The Contractor shall demonstrates through submission of detailed technical documents, data sheets, track record, reference materials, locations of STPs, capital and operation and maintenance cost per mld of sewage treated etc, to demonstrate that the STPs built with chosen treatment technology  are   cost  effective with minimum operation and maintenance cost, in particular the power consumption cost and are  functioning well and satisfactorily for the last 5 years in neighboring countries. Furthermore, the Contractor shall demonstrate that the technology is   adaptable to local conditions in Hulhumalé and the foot print required for the STP units is minimum and not exceeding the available space in the land parcel allocated in Hulhumalé to house the STP and the associated ancillary facilities.

- Generic Process Considered Suitable for the Proposed STP.

Some of the generic process type considered suitable for STP are SBR, MBBR, Extended Aeration, any advanced modern Technology process with Nutrient Removal, etc.

- Treatment Process Considered Not Suitable

The following processes are considered not suitable for the proposed STP and they shall not be accepted by the Employer.

- Oxidation pond (facultative/anaerobic/aerobic)

- Trickling filters

- Oxidation ditch

- Rotating Biological Rotators (RBC)

- Up-flow Anaerobic Sludge Blanket (UASB) Technology

- Anaerobic Filter/Technology

- Base Data on Sewage Influent Characteristics

The following base data on sewage influent characteristics are based on the testing of limited number of composite sewage samples collected from the sewer network   in the project   area and the data is meant only for preparing preliminary design of STP for purpose of cost estimation. Thus, data given below is indicative only and the Employer does not guarantee the accuracy of the data. Thus, the use of data without any validation shall be entirely at the risk and cost of the Contractor.

The Contractor is deemed to have either validated the base data or accurately determined the sewage influent characteristics by  carryout his own tests  of representative composite sewage samples taken by him on site in accordance with the methods and frequencies explained in Clause 7.7.3, and established a suitable design range for the key parameters for designing the STP. It shall be understood that the Contractor is entirely responsible to establish appropriate key parameters for designing of the STP.

| Average Flow | 10 MLD |
| --- | --- |
| Peak Factor | 2.25 |
| Peak Flow | 22.5 MLD |
| pH | 6.5-8.5 |
| Sewage Temperature | Min:150 Max:350 |
| Total BOD 5 Days @20o | 400mg/L |
| COD | 800mg/L |
| Total Suspended Solids | 350mg/L |
| Oil and Grease | 20mg/L |
| Total Nitrogen (as N) | 75mg/L |
| Total Phosphorus | 17 mg/L |
| Fecal Coliform | 1x107 MPN/100 ml |

- Effluent Discharge Requirements

Treated effluent discharged from the Works shall at all times comply with water quality requirements for ground water recharge in the latest National Waste Water Quality Guidelines of EPA (Maldives) manual and also comply with EPA’s requirement for discharging the effluent into the sea. EPA’s water quality requirements are reproduced below for reference

| Description | Max. Allowable limit (to comply EPA’s Requirements in Table 6.3 National Water Quality Guidelines, Ground Water Recharge. |
| --- | --- |
| pH | 5-9.5 |
| BOD | 5 mg/l |
| COD | 5 mg/l |
| TSS | 15 mg/l |
| Nitrates | 6 mg/l |
| Faecal Coliforms | 10 org / 100 ml |
| E. Coliforms | 0 org / 100 ml |
| Residual Chlorine | 0.2-0.8 mg/l |
| Dissolved oxygen | 2.0 mg/l |
| Conductivity | Equal or less than receiving ground water |
| Oil, grease and waxes (food related) | <5mg/l |

- Quality of Sludge

The treatment process adopted by the Contractor shall produce wet sludge with minimum solids content of 25%. The wet sludge shall be dewatered by suitable dewatering process such as centrifuge to capture more solids and produce sludge with minimum 25% solid content to make compost by In-Vessel Composting process.

- Quality of Compost Material

Compost materials shall be of spreadable quality on agricultural land and shall be dry with moisture content less than 60%

1.2.2	In-Vessel Sludge Composting Plant

The Contractor shall design, construct, commission and operate an odour free and cost effective In-Vessel Sludge Composting Plant in the designated land adjoining the premises of STP to compost the daily production of dewatered sludge from the STP. The composting process shall take place in a confined vessel and the Contractor shall ensure that gasses produced during the composting process are adequately managed within the composting vessel to have zero odour. The plant shall have built-in facility to contain and treat obnoxious gases or removal of the gases for treating  in the odour treatment facility in the STP.

To achieve the performance requirements, it may be necessary to suitably mix the dewatered sludge with amendment and bulker. From a composting perspective, an amendment may be any material used to modify moisture, structure (porosity), pH or the C:N ratio of incoming feed material. Amendments can be sawdust, woodchip, paper, cardboard or even lime and urea or any other. A bulker is a material that is added specifically to improve the structure or porosity of the dewatered sludge. A bulker can be, shredded wood, construction timber waste or woody green waste or any other similar materials. The co-composting material to enhance the nutrients content of the compost shall be dewatered household food waste.

Waste Management Corporation Ltd (WAMCO), Maldives, a state-owned operator is responsible for collection and disposal of solid waste from the households in Hulhumalé to a designated landfill site at Thilafushi island. The daily collection of household waste and amendment and bulker materials in Hulhumalé by WAMCO are indicated in the table below. The Contractor shall liaise with WAMCO and ascertain that adequate composting materials are available to compost the daily production of sludge from the STP

The quantities and the moisture content  shown are indicative only.

- Availability of Feed Material for In-Vessel Composting (Indicative only)

|  | Feed Material Availability in Hulhumale for In -Vessel Sludge Composting (Indicative) |  |  |
| --- | --- | --- | --- |
|  | Material availability | Availability/day | Moisture content. |
| (i) | Dewatered Sludge from STP (Ultimate) | 3.2 Tons | 75% |
| (ii) | Solid Waste Collected in Hulhumalé | 144 Ton | 75% |
| (iii) | Amount of Food Waste available in Hulhumalé. | 57.6 Tons | 75% |
| (iv) | Amount of garden/yard trash available in Hulhumalé | 54.7 Tons | 25% |
| (v) | Amount of wastepaper & cardboard etc. available in Hulhumalé | 2.88Tons | < 25% |
| Note: Only sludge produced from the STP is to be composted. The Contractor shall appropriately mix the other solid waste with the sludge to achieve the optimum moisture content and texture of the feed material that is suitable for efficient composting. |  |  |  |

- Indicative design guide

|  | Indicative design guide |  |
| --- | --- | --- |
| (i) | Suggested moisture content of food waste to be used with sludge for composting | 60% (to be achieved by using screw presses as required) |
| (ii) | Optimum Moisture Content of feed material | 40 to 60%. Shall be achieved by suitably mixing sludge with available garden waste and food waste. |
| (iii) | Capacity of each vessel | To compost 800kg of dewatered sludge per day. |
| (iv) | No of vessel required to compost 3.2 tones sludge per day | 4 Vessels including feed hopper, bio-filter, feed and discharge augurs. |
| (v) | Typical foot print of a vessel with accessories | 120sqm |
| (vi) | Land Available to house 4 units of In-Vessel Compost Plant. | 1700 Sqm ( approximately 85m long by 20m wide) (Includes Feed bunkers and Maturation Bunkers as shown in the general layout arrangement drawing below |
| (vii) | Power Supply | Typically 440V, 32A, 3 Phase supply |
| (viii) | Power Consumption | <90Kwh per tonne of sludge compost (optional) |
| (ix) | Chemical Consumption | Max. use of Polyelectrolyte is 2.5 kg/Tone of Dry Solids. |
| (x) | Quality of Dewatered Sludge | Min. sludge TSS (dry solids) 25% |
| (xi) | Odour Emissions Requirement at the boundary wall of STP. | No Odour (smell) at the STP boundary |
| (xii) | Current Availability of Sewage | 10,560 m3/day |

1.2.3	Ancillary and Other Works

Design and construct all associated buildings and structures which are required for the plant.

The Contractor shall study the existing pumping system of outfall 1 and 2 (and Outfall 3 which is under construction) and design and construct diversion works, including pumping mains, modify the wet well of key pumping stations, pumps, piping, valves, and associated electrical and instrumentation equipment and, everything else required, for diverting the sewage flows from Phase 1 area to the inlet works of the STP.

The Contractor shall design, build and connect effluent pipeline from the STP to the Outfall-1 and 3 (new), including modification of the outfall discharge diffusers as required to dispose the treated sewage to the sea. The Contractor shall also design and build or modify emergency by-pass pipelines for discharging raw sewage in the event of an emergency or maintenance shutdown of STP. All the above work shall be done with necessary approvals from the authorities and in consultation with  MWSC.

## 1.3.	Treatment process selection and design

The treatment process proposed by bidder shall be widely used by countries including in neighboring countries with proven track record for treating sewage of similar characteristics to that of Maldives and suitable for Maldivian Environmental conditions. The treatment process for the proposed STP shall comprise Primary, Secondary and Tertiary Treatment units (optional) to achieve the effluent quality requirement specified in this document.

The sludge produced shall be of suitable quality for making biosolids/sludge composting on site using In -Vessel sludge composting plant.  The entire STP units, associated buildings and any other works as required for the establishment of 10 mld STP at Hulhumalé shall be housed in the limited land of size 76.6m x 84.5m as shown in tender drawing no. TTI/MUD/MAL/GA/STP/001(Refer to Volume 2) which is an indicative layout and to be used for contractors guidance only.

Some of treatment process that are widely used and considered suitable to achieve desired objectives will include but not limited to:

- Extended Aeration Process (EA)

- Sequential Batch Reactor (SBR) (with Anoxic Tank)

- Moving Bed Bio-reactor (MBBR) (with Anoxic tank)

Contractor shall provide all information necessary for complete evaluation of the Contractor’s proposed technology by the Employer, including drawings, design calculations, technical specifications, data sheets, proposed construction/installation methodology, track record on the successful use of the technology, particularly in the neighboring countries, and other relevant details required for a comprehensive evaluation of the technology.

Any Proposal without the above information will be considered as non-responsive and liable for rejection. Proposal must satisfy the Employer’s performance requirements as set out in the Proposal documents. Contractors shall include with their Proposal evidence acceptable to the Employer of satisfactory past performance of same technology-based plant designs and the associated equipment and processes offered and full details of similar plant capacities called for to enable proper evaluation of design.

## 1.4.	Nominated Sub-contractors and co-operation with other contractors

No contractor is currently working on the nominated Site.

No nominated Subcontractors are proposed for the Works.

# 2.	The Project Site

## 2.1.	Description of Site and Site Access

The project site is in Hulhumale', a reclaimed island north of Malé, the capital city of Maldives. The Male’s International airport, known as Velana International airport is also situated in a reclaimed island which is linked to Hulhumaléisland by a coastal road.

The land reclamation for Hulhumalé began in the lagoon of Hulhulé. The Hulhumalé has two phases of development, Phase 1 and Phase 2. Phase 1 is about 195 Ha in size and the proposed land for the STP is located in Phase1 area. Phase 2 is about 244 Ha in size which is currently under development.  The proposed STP shall be designed to treat sewage flows from Phase 1 area only.

The soils in the island is geologically young. They consist of substantial quantities of the un-weathered coral parent material, coral rock and sand. Soils are coarse in texture and shallow in depth with a top layer of brown soil (0 to 40 cm in depth) from the original sea bed and is followed by a transition zone on top of the underlying parent material of coral reef limestone.

The land allocated for the project site is a 76.6m x 84.5m size flat land, located approximately 1.5 km to the north east of the airport. The location of the site is shown in Drawing No. TTI/MUD/MAL/LP/001A. The site is mostly a barren land but there are some temporary sheds and no existing utilities. The land is in close proximity to a football stadium and other public facilities. It is also close to Hulhumalé Industrial enclave. Thus, consideration shall be given in the design of STP to eliminate odour nuisance from the treatment units. An adjoining parcel of land of size 1700 Sqm (approximately 85m long by 20m wide)) has been also earmarked to house the In-Vessel Sludge Composting Plant including feed bunkers and maturation bunkers and storage areas, sheds etc.

Location of STP

(76.6mx84.5m)

Hulhumale (Phase1 Area)

The master plan allows for various land uses such as Commercial, Residential, Light Industrial, Institutional, Cultural, Retail, Leisure and Educational in Phase1. The site is easily accessible by motor vehicles. The site is generally flat with a ground level of approximately 1.95m above datum and the water table is about 1.4m below. The coordinates of the STP site are given below:

| POINTS | EASTING | NORTHING |
| --- | --- | --- |
| A | 337841.102 | 464836.152 |
| B | 337864.109 | 464917.453 |
| C | 337937.853 | 44896.585 |
| D | 337914.846 | 464815.283 |

Existing dry utilities such as L.V power, telecom is available adjacent to the site and wet utilities such as potable water, sewerage etc., are also available adjacent to the site. The electricity power offtake shall be from the nearest substation.

## 2.2.	Right of Access to the Site

The contractor shall notify the Engineer in writing 14 days in advance his intentions to start work. The Right of Access to the Site for the construction (including survey, design and all other necessary works including testing and commissioning) of pipelines, outfalls and associated works for the influent sewer and discharge of effluent from the site of the STP shall be arranged by the Employer in accordance with the Contractor’s programme. The Contractor will be required to comply with all regulations of other Authorities regarding the use of this part or parts of the Sites.

The access to these parts of the site will not be exclusive and the duration of the access may be limited to periods required for survey, design and construction. The above requirements shall not relieve the Contractor of his responsibility for site security under the Contract.

# 3.	STP Technical Requirements

The output standards shall be as specified in the Schedule of Performance Standards.

## 3.1.	Description of Catchment

### 3.1.1	Geographic area served by the STP

Phase1 area is predominantly residential areas with commercial establishments, schools, hospitals and a small industrial cluster. Phase 1 development of Hulhumalé is for an ultimate population of 80,000 people in the reclaimed land of 195 hectares. By the end of 2017 approximately 50,000 people have started to live in the project area. The current population in phase 1 area as of 2019 is approximately 60,000 and is expected to be saturated within the next few years.  A floating population of approximately 15%-20% is also expected during holiday seasons.

## 3.2.	STP flows and capacity requirements

## 3.2.1	Sewer network and Sea outfalls in Phase 1 area

Sewer network in Phase 1 area comprises about 44.8 km of pipelines (uPVC) of diameters from 160mm (OD) to 315mm (OD) and the network is fully functional.  A schematic of pump stations/outfall for the Phase 1 area is shown in Drawing No. TTI/MUD/MAL/PL/ESN/001B.

Another outfall of 400mm (OD, HDPE pipe) is under construction near Outfall-1 to complement the existing two outfalls whose combined capacity is inadequate to discharge the sewage from Phase 1 area when it is fully developed to accommodate the ultimate   population of 80,000 people.

There are seven (7) main submersible sewage Pumping Stations (PS1, PS-2B, PS-3B, PS- 4B, PS-5C, PS 6 and PS 7) are connected to Outfall-1 which is a  280mm dia (OD)  HDPE pipeline located near Planktons Beach Hotel. Another three (3) main submersible sewage Pumping Stations (PS 8, PS 9, PS 10) are connected to Outfall -2 which is also a 280mm dia (OD) HDPE pipeline located near the Bus Depot.

The pumping mains from the submersible pumping stations are connected to the outfalls 1 &2 by an interconnecting pumping main system as shown in the Drawing TTI/MUD/MAL/PL/ESN/001B.

## 3.2.2	Diversion of sewage from phase 1 area to STP

The sewage from Phase 1 area shall be diverted by the Contractor to the proposed Sewage Treatment Plant (STP) by intercepting the pumping main system connected to the outfalls as suggested in drawing no. TTI/MUD/MAL/PL/ESN/001B.

The contractor shall study the existing pumping system of outfalls and design/construct/ modify the wet well, pumps, piping, valves, and associated electrical and instrumentation equipment for forwarding the flows to the inlet works of the STP. The contractor shall utilize the existing mechanical/electrical/instrumentation equipment which has further design life span wherever possible and make all diversion system functional to convey  the sewage to the inlet works of the STP.

3.2.3	Capacity of Sewage Treatment Plant

### The current population of the Hulhumalé phase 1 area is estimated to be 60,000 and expected to reach its ultimate population of 80,000 within the next few years. Based on the water consumption of the current population the per capita sewage flow is estimated to be 132 lpcd (i.e. 80% of water consumption of 150 lpcd plus 10% for water infiltration). A floating (tourist) population of 10,000 is also expected but this is seasonal and may be for 2-3 months.

### The capacity of the proposed sewage treatment plant for phase 1 population and based on the above per capita flow of 132 lpcd shall be 10.0 MLD. Based on the experience in other countries in the region, the plant could be overloaded by 15-20% for certain duration which will cater for the load from the floating population.

The Contractor shall design and build the Works to meet the minimum capacity requirements specified in the Schedule of Performance Standards and shall ensure that such capacity is available throughout the Operation Service Period.

The STP shall be designed for the preliminary units for ultimate stage peak flow, secondary units for average flow and tertiary units for average flow. As a guidance, the following flow values are suggested for consideration by the Contractor in the design of STP.

| Sl. No. | Flow Details | Value | Unit |
| --- | --- | --- | --- |
| 1 | Average flow | 10.00 | MLD |
| 2 | Average flow | 0.116 | m3 /sec |
| 3 | Peak factor | 2.25 |  |
| 4 | Peak flow | 22.50 | MLD |
| 5 | Peak flow | 0.260 | m3 /sec |

## 3.3	Wastewater composition

### 3.3.1.	Base data on wastewater influent characteristics

The Employer’s consultant have carried out the quality analysis tests on the composite sewage samples taken in Phase 1 area. The tests were conducted for preliminary design and estimation purposes. The parameters mentioned are tentative and indicative only and sewage parameters mentioned below shall not be used by the Contractor for designing of STP without validation by him.

The Contractor shall carry out his own and independent tests to determine the characteristics of sewage and suitable design range for key parameters for use in his design.  Contractor shall liaise with the Government Agencies and testing laboratories in Maldives to carry out comprehensive quality analysis of sewage collected from the site in accordance with acceptable procedures.

| Indicative Sewage characteristics |  |  |
| --- | --- | --- |
| Sl. No. | Parameter | Values (Range) |
| 1 | pH | 6.5 – 8.5 |
| 2 | Sewage Temperature |  |
|  | Min Temperature | 150 C |
|  | Max Temperature | 350 C |
| 3 | Total BOD 5 Days @ 200C, mg/L | 370-400 |
| 4 | COD, mg/L | 740-800 |
| 5 | Total suspended solids, mg/L | 200-350 |
| 6 | Oil and grease, mg/L | 10 - 20 |
| 7 | Total Nitrogen (as N), mg/L | 65-75 |
| 8 | Total Phosphorus, mg/L | 13 - 17 |
| 9 | Fecal Coliform MPN/100 ml | 1x107 |

## 3.4.	Effluent discharge requirements

Treated effluent discharged from the Works shall at all times comply with the discharge standards specified in the Schedule of Performance Standards.

The treated effluent shall be discharged into sea via outfall-1 and outfall-3 (New) located near Planktons Beach hotel and is approximately 1.5 km from the STP site. The outfall-2, located near Bus depot and approximately 0.5 km away from the STP, can also be used to discharge part of the effluent. The location of the outfalls is shown on drawing no. TTI/MUD/MAL/PL/ESN/001B (Refer to Volume 2).

## 3.5.	Sludge treatment and disposal requirements

## 3.5.1	The objectives

The main objectives of sludge treatment shall be:

- Reduction in the volume of sludge for disposal by removing some of the water.

- Destruction of pathogenic organisms

- Stabilization of the organic matter contained in the sludge.

- Suitable to make compost along with biosolids and other municipal waste in an In-Vessel Composting Plant to be built adjacent to the STP. The compost shall be sold as fertilizer to off-set some of the product cost of compost.

- Disposal of the sludge/excess compost in a safe and aesthetically acceptable manner

3.5.2	Quality of Sludge

The treatment process adopted by the Contractor shall produce wet sludge with maximum solid content. The wet sludge shall be dewatered by suitable dewatering process such as centrifuge to capture more solids and produce sludge with minimum 25% solid content to make compost by In-Vessel Composting  process.

The dewatered sludge quality requirements to be met are listed below:

| Treated Sludge (Dewatered Sludge) Quality Requirements |  |  |
| --- | --- | --- |
| Parameter | Units | For STP |
| Minimum sludge TSS (dry solids) | % w/w | 25% |
| Maximum use of Polyelectrolyte | Kg | 2.5 Kg/T of dry solids |

An emergency storage of dewatered sludge shall be provided in the premises of In-Vessel Composting Plant for three days Two (2) nos. of tractor and tipper of sufficient capacity to transport the dewatered sludge to the In-Vessel Composting Plant shall be also provided.

3.5.3	In-Vessel composting of sludge

Compost materials shall be of spreadable quality on agricultural land and dry with moisture content less than 60%. Sludge pH shall be 6-9. C/N ratio shall be 20-35:1 by weight. Temperature for stabilization shall be 50 to 60 deg C

3.5.4	In-Vessel Sludge Composting Plant

Land based disposal of wet sludge from STP is costly and environmentally undesirable.  Composting sludge is an effective way of  converting the wet sludge from an STP into  a stable organic material which can be used  in the agriculture land as fertilizer or as a garden  manure.

The Employer has made provision in the Contract for the Contractor  to build an In-Vessel Sludge  Composting plant in a designated land parcel, adjacent to the STP as shown in Drawing TTI/MUD/MAL/GA/STP/001 to treat the sludge and produce stable organic  compost material.

The Contractor shall design, construct, commission and operate an odour free and state of the art In-Vessel Sludge Composting plant in the designated land parcel. The In-vessel plant shall have capacity to compost the daily production of dewatered sludge from the STP. The composting process shall take place in a confined vessel environment and the Contractor shall ensure that gases produced during the composting process are adequately managed within the composting vessel to have zero odour emission. The plant shall have built-in facility to treat the gases generated from the plant or to trap and conveying it to the odour treatment facility in the STP for scrubbing the odour.

3.5.5	Composition of Compost Material

For effective composting of sludge and to enhance nutrients content of the compost, it is necessary to suitably mix the sludge with nutrient rich household food waste. The solids in the sludge are primarily a source of nitrogen and must be mixed with a higher carbon containing amendment material such as sawdust, woodchips, newspaper. An amendment modifies moisture content, structure (porosity), pH or the C:N ratio of incoming feed material. A bulker is a material that is added specifically to improve the structure or porosity of the dewatered sludge. A bulker can be, shredded wood, construction timber waste or woody green waste or any other suitable materials.

3.5.6	Availability of Feed Material, Amendment and Bulker in Hulhumalé for In-Vessel Composting (Indicative only)

Waste Management Corporation Ltd (WAMCO), Maldives, a state-owned operator is responsible for collection and disposal of solid waste from the households in Hulhumalé to a designated landfill site at Thilafushi island. The daily collection of household waste and amendment and bulker materials in Hulhumalé by WAMCO are indicated in the table below. The Contractor shall liaise with WAMCO and ascertain that adequate composting materials are available to compost the daily production of sludge from the STP.

|  | Feed Material Availability in Hulhumale for In -Vessel Sludge Composting (Indicative) |  |  |
| --- | --- | --- | --- |
|  | Material availability | Availability/day | Moisture content. |
| (i) | Dewatered Sludge from STP (Ultimate) | 3.2 Tons | 75% |
| (ii) | Solid Waste Collected in Hulhumalé. | 144 Ton | 75% |
| (iii) | Amount of Food Waste available in Hulhumalé. | 57.6 Tons | 75% |
| (iv) | Amount of garden/yard trash available in Hulhumalé. | 54.7 Tons | 25% |
| (v) | Amount of wastepaper & cardboard etc. in Hulhumalé. | 2.88Tons | <25% |
| Note: Only sludge produced from the STP to be compost. The Contractor shall appropriately mix the other solid waste with the sludge to achieve the optimum moisture content and texture of the feed material that is suitable for efficient composting. |  |  |  |

    - Design Criteria

The following biosolids characteristics must be considered in designing an in-vessel composting system. The Contractor shall indicate suitable design values for the following in his design submission.

- Moisture content

- Volatile solids content

- Carbon content

- Nitrogen content

- Bulk Density

3.5.8	Indicative design guide

| Sl. No | Indicative design guide |  |
| --- | --- | --- |
| (i) | Suggested moisture content of food waste to be used with sludge for composting | 60% (to be achieved by using screw presses as required) |
| (ii) | Optimum Moisture Content of feed material | 40 to 60%. Shall be achieved by suitably mixing sludge with available garden waste and food waste. |
| (iii) | Capacity of each vessel | To compost 800kg of dewatered sludge per day. |
| (iv) | No of vessel required to compost 3.2 tones sludge per day | 4 Vessels including feed hopper, bio-filter, feed and discharge augurs. |
| (v) | Typical foot print of a vessel with accessories | 120sqm |
| (vi) | Land Available to house 4 units of In-Vessel Compost Plant. | 1700 Sqm (approximately 85m long by 20m wide) (Includes Feed bunkers and Maturation Bunkers etc.) |
| (vii) | Power Supply | Typically 440V, 32A, 3 Phase supply |
| (viii) | Power Consumption | <90Kwh per tonne of sludge compost (optional) |

## 3.6.	Efficiency requirements

The offered treatment process shall be the most appropriate and state of the art in terms of both efficiency of treatment and cost (the Bidder shall have to produce the performance records with the same treatment systems applied elsewhere). The process shall be cost effective from both capital and O&M costs consideration.

## 3.7	Other environmental requirements

## 3.7.1	Odour Control

Control of Odour emission from the STP is one of the major requirements of the Employer to prevent the STP causing any Odour nuisance to the adjoining facilities which include a football stadium, public parks, key utility buildings and government offices.   The Contractor shall install and operate a state of the art odour control system which shall achieve the Employer’s objective of no sewage induced Odour outside the premises of STP complex.

The odour treatment plant for the STP shall be therefore trap and treat the odorous air from the STP units, bio solids and sludge drying treatment processes at the plant and to achieve zero odour emissions outside the premises of the STP. The Contractor shall choose the Odour control plant or the odour neutralizing process which he considers most suitable for the STP and to achieve the Employer’s objective of no sewage gas induced smell outside the premise of the STP. The Contractor shall submit sufficient details including track record to establish that the plant he offered to build under the DBO Contract has been successfully used in the past 5 years to neutralize the sewage gas induced smell from the STP units.

The contractor shall indicate the STP units which are to be enclosed/covered and products to collect and convey odorous gases to the Odour control unit in his layout/design drawings for STP units to be submitted with the bid.

## 3.7.2	Noise nuisance

- Construction Phase:

During construction phase, the use of heavy machinery could result in noise annoyance for nearby residents. In general, noise levels from even very heavy construction equipment are at acceptable levels at distances greater than 500 m. It is therefore assessed that impacts from construction noise will be minimal. However, it will be the contractors' responsibility to ensure that the noise regulations of Maldives are complied with at all times. The Contractor shall ensure that the operations entailed in the construction of the Works do not cause annoyance to others working on the Site or to persons living adjacent to the Site.

- Operation Phase:

Where necessary, equipment shall be provided with acoustic, sound-dampening enclosures to limit ambient noise during normal operation to the limits detailed in the requirements elsewhere. Noise monitoring shall be carried out by the Contractor on a random basis.

## 3.8.	Materials requirements

3.8.1	Acceptable Materials

The material proposed should be suitable for Maldivian Environmental conditions. The preferable material and its grade for various basic items are presented in the below table. All other material shall satisfy the requirements of the project and as per the local and international standards and fit for purpose.

| Sl. No | Material | Grade |
| --- | --- | --- |
| 1 | Concrete for Water Retaining Structures | C 40 |
| 2 | Concrete for Non-Water Retaining Structures | C 35 |
| 3 | Mass Concrete | C 20 with Sulphate resistant cement as per site conditions |
| 4 | Reinforcement – Mild Steel – Tensile Strength | 250 N/mm2 |
| 5 | Reinforcement – High Yield – Tensile Strength | 460 N/mm2 |
| 6 | Water stops | PVC |
| 7 | Pipes and Fittings – Potable water | MDPE/uPVC |
| 8 | Pipes and Fittings – Sewage – Gravity Systems | uPVC |
| 9 | Pipes and Fittings – Sewage – Pressure Systems and Interconnecting STP units | HDPE |
| 10 | Steel Pipes | Stainless Steel Grade 316 L |
| 11 | Valves/Penstocks | Ductile Iron with suitable anticorrosive coating |

3.8.2	Reinforcement Cover

Correct concrete cover to reinforcement shall be maintained with the aid of approved spacer pieces. The cover shall not be less than as given below, according to the type of structural member and the placing and exposure conditions as follows.

Condition 1: Concrete placed in forms and not to be exposed later to the weather, groundwater, fresh water, or to any combination of these.

Condition 2: Concrete placed in forms but later to be exposed to the weather, groundwater, fresh water, or to any combination of these.

Condition 3: Concrete placed directly in contact with the ground.

Condition 4: Concrete to be exposed to corrosive vapours, corrosive groundwater, sea water or sea spray. Sufficient protection to the reinforcement shall be provided by adopting the minimum cover for exposure condition 3 and applying a protective coating or membrane on the concrete surface. The method of protection shall be in accordance with the provisions of the specification and to the approval of the Engineer.

| Minimum Cover to Reinforcement Structural Member | Minimum Cover (mm) for Placing of Reinforcement for Exposure Condition |  |  |
| --- | --- | --- | --- |
|  | Condition 1 | Condition 2 | Condition 3 |
| Pad footings and Pile Caps | - | 65 | 75 |
| Strip footings | - | 50 | 65 |
| Bored or Cast Piles | - | 50 | 75 |
| Columns of all types | 30 | 40 | 75 |
| Walls, including retaining walls | 25 | 30 | 75 |
| Beams | 30 | 40 | 65 |
| Slabs, including concrete joist and hollow block construction | 25 | 30 | 65 |
| Cover to embedded pipes | 25 | 30 | 65 |

## 3.9	Electricity and Power

### 3.9.1.	Available electrical supply to the STP

State Electric Company Ltd (STELCO) is the main electric power company in Maldives. The Contractor shall liaise with STELCO to obtain electricity supply to the STP. Incoming point of supply till tariff meter may have to be carried out by STELCO. The Contractor shall design and install the entire electricity distribution network, supply points, transformer etc within the STP premises. Contractor shall consult Maldives Energy Authority and STELCO and obtain necessary compliance approvals to have power supply to run the STP.

### 3.9.2.	Standby generation requirements

Diesel Generator Set:

The Contractor shall supply, install and make connection to the main switch board diesel generator (DG) set as a stand by power supply facility in the event of a failure of power supply  from the power company. The capacity of the diesel generator shall be adequate enough to run the STP and the ancillary facility during a power failure.

UPS System:

A UPS of adequate capacity with battery back-up of min. 1hour shall be provided.

### 3.9.3.	On-site power generation

### While this is not in the scope of the project, contractor’s shall note that the Employer will consider installing Photovoltaic (Solar Panels) in the roof of the buildings and in the open spaces available within the STP premises to capture maximum solar energy for conversion into electricity under a separate Contract.

### The proposed solar energy generation system will be a solar diesel hybrid system capable of combining solar power from the photovoltaic system with electricity from fuel driven power supply. An Energy Management System (EMS) should be installed to monitor, control and optimize the usage of solar power and to reduce power consumption as much as from the National grid.

## 3.10.	Monitoring, sampling and testing equipment

### 3.10.1	Flow parameters

Flow measurement devices shall be installed to measure the following:

- Volume and flow rate of sewage influent

- Volume and flow rate of treated sewage discharged from the Works

- Volume and flow rate of sewage bypassed

All meters and other flow measurement devices shall be sited to avoid interference from flow turbulence and shall be accurate to within the following tolerances:

For Electromagnetic Flow meter and accuracy level of 0.5% or better shall be achieved and for Ultrasonic Flow meter 0.2% or better for the measuring range.

### 3.10.2.	Sampling and testing equipment

The sampling shall be in accordance with the following procedures:

- All samples shall be representative of the appropriate stream. Samples shall be taken from such a position that there is no interference due to accumulated solids and/or scum.

- Daily grab samples shall be taken at approximately the same times each day.

- Where appropriate, mixed liquor and return sludge samples shall be used daily in the standard WRc (UK) settlement tests to determine the specific sludge volume index (SSVI) of the sludge at 3.5 g/l.

- Samples shall be fixed, stored and handled as per standard methods. Analysis of the samples should be undertaken within 24 hours (except supplied which should be measured at once) and reported to the Engineer within 48 hours, except for metals, pathogens and BOD which should be reported within 7 days.

- Analysis of samples shall be carried out in accordance with the methods specified in the latest edition of:

- the ‘Standard Method of Examination of Water and Wastewater’ (APHA),

- Schedule 2 of S.I. No. 419 of 1994 – Urban Wastewater Treatment Regulations, 1994

- the “Methods for the Examination of Waters and Associated Materials” published by the HMSO (UK).

- or other methods of comparable accuracy as agreed by the Engineer.

- For composite samples, automatic samplers shall be used. They shall be provided with a refrigeration facility and the sample lines shall be continuously purged. Samples shall be programmed to collect samples over twenty-four hours as 15-minute sub-samples. Where flow monitoring of the stream to be sampled is provided, samples shall be taken on a flow proportional basis. Regular clearing of sampling lines, equipment and bottles shall be carried out to avoid contamination.

- Where appropriate, laboratory analyses shall be undertaken at an accredited laboratory approved by the Engineer who reserves the right, in the case of an independent laboratory, to visit the premises in order to ascertain that testing is being carried out accurately for treated sewage and sludge and in accordance with the accepted procedures.

- For the proposed STP irrespective of the treatment processes, such as ASP, SBR and MBBR and etc.   the recommended tests to be carried out are mentioned in the following tables.

The no. of samples required to do analysis is presented in clause 6.9.6.2 and 7.7.3

Recommended Plant Control Tests on a Daily basis in a Typical STP

Recommended Plant Control Tests on a Weekly basis in a Typical STP

Recommended Plant Control Tests on a Monthly to Biannual basis in a Typical STP

### 3.10.3.	Site laboratory and equipment

### Please see the attached Annexure A  for the list of proposed laboratory equipment. Refer to Annex A of this document.

## 3.11.	Other design-build requirements

### 3.11.1.	Site Access

### The site access shall be from the adjacent main road. An internal asphalt road of 4.50m with required turning radius shall be provided within the site. All units shall be accessible via the access road. Necessary road kerbs shall be provided at both the edges. Road drains shall also be provided which shall be as per the site drainage requirements. The STP area shall be provided with adequate lighting with the required illumination level.

### 3.11.2.	Instrumentation, SCADA and telemetry

Requirements for the SCADA system:

Following are the minimum requirements related to the SCADA system for the Sewage treatment Plant. The Contractor shall design the SCADA system for the fully automated plant and the complete details shall be provided. The necessary software and Hardware shall be supplied along with the SCADA system. Interfacing with PLC Panel shall comprise latest Personal Computer with 22” LCD Monitor, Multi Media Kit, Printer, Internet Connection, RS-View, RS-Links (Gateway Version), Process and Operator Software with dynamic Flow Charts, Pictures, Screens, Alarms, Historical Trends, Reports etc.

The proposed 10 MLD STP at Hulhumalé will operate in fully automatic/ semi-automatic mode and shall be controlled through PLC & SCADA System. Local Control Panels (LCP)/ Local Push Button Stations (LPBS) will be provided to operate equipment from local. SCADA System shall be designed to control, monitor, display and equipment operating information and to perform various process control functions and generate various reports.

The SCADA system will be having connectivity provision for future communication.

List of Instruments:

For smooth and seamless operation of the STP plant at Hulhumalé the following instruments will be provided:

- Level Instruments:

Level instruments will be provided as minimum at the following locations for local/ remote level measurement & interlock purpose.

- At inlet & outlet of mechanical fine screen channel for auto cleaning of screens (differential level transmitter for each screen)

- Raw water sewage sump for pump dry run protection (level transmitter with wall mounted display)

- Chlorination cum treated water tank (level transmitter with wall mounted display)

- SBR 1 and 2 (level transmitter with wall mounted display). For other treatment process contractor shall provide level transmitter systems if required.

- Sludge sump (level transmitter with wall mounted display)

- Level switches at polymer dosing tanks

- Pressure Instruments:

- All the pressure instruments provided for plant will be with chemical seal diaphragm.

- Pressure Gauges will be provided at delivery of all pumps and the locations.

- Pressure transmitter will be provided at common discharge of raw sewage transfer pumps

- Pressure transmitters will be provided for common blower outlet.

- Flow Instruments:

Ultrasonic/Electromagnetic type flowmeter will be provided for local/ remote flow measurement & indication purpose.

- WasteWater Quality Analyzers Instruments:

Analyzer instruments will be provided for process parameter measurement like Dissolved oxygen, BOD, COD, N&P, Residual chlorine etc. All the instruments will have PLC interfacing compatibility.

- SCADA & PLC

The PLC based SCADA system having PLC with redundant processor, power and communication modules, integrated IO cards including system expandable IO modules (if required), floor mounted cabinets, terminal board within cabinets, Ethernet switch, LIU, patch cords (copper/ fibre), Interface Outlets, connectors and all necessary accessories, etc. for control, interlocking and monitoring, trends/ alarms annunciation, data logger etc. of STP.

- Signals interfacing with PLC

Field instruments such as switches, transmitters will be hardwired to PLC with I&C cables through usage of junction boxes wherever required. MCC signals will be interfaced with PLC with multi-pair/ core I&C cables. Various package system LCPs/ PLCs will be interfaced with main PLC through hardwired/ soft communication links.

- Pumping station & recycle water pumping station automation

Following field instrument shall be installed at pumping station for Monitoring, Automation and control of the Sewage & Recycled water pumping Stations

- Electromagnetic Flow Transmitter at common Header of Pumps

- Pressure Transmitter at common header of Pumps

- Ultrasonic Level Transmitter for storage tank

- Connecting Bus coupler, Incomer and MFM for monitoring the energy parameters

- Status Monitoring and control of Individual Pumps and Exhaust fans

- Level Switch for monitoring the water level in Sump and pump control

- Status Monitoring of the Valves

### 3.11.3.	Septage Receiving Point

### Not Applicable

### 3.11.4	Administration buildings, stores, workshops and laboratory

Buildings shall be provided for the STP site to suit the Contractor’s detailed design; however, the following buildings are to be provided as a minimum unless the required facilities are included within another building. Contractor shall note that the dimensions mentioned are the minimum size and this should match with the equipment to house the room. The sizes of buildings shown in the following table is for information only and the contractor shall design the building to accommodate the Mechanical & Electrical and Administration requirements and to store the chemicals/Chlorine for a period of one month.

| Sl. No. | Description | Length (m) | Width (m) | Height (m) | Remarks |
| --- | --- | --- | --- | --- | --- |
| 1 | ##### Blower Room+ PMCC Room (GF) and PLC/SCADA/UPS, Laboratory and Admin (FF) | ##### 14.00 | ##### 12.00 | ##### 4.50 | ##### G+1, Dimensions are for each floor |
| 2 | ##### HT Panel/MCC and Metering Room/Odour Control Panel | ##### 12.00 | ##### 8.00 | ##### 4.50 |  |
| 3 | ##### Chlorination Building | ##### 10.00 | ##### 8.00 | ##### 4.50 |  |
| 4 | ##### Centrifuge House | ##### 8.00 | ##### 6.00 | ##### 4.50 | ##### G (Stilt) +1 |
| 5 | ##### Security Cabin | ##### 4.00 | ##### 4.50 | ##### 3.20 |  |
|  | ##### YARD |  |  |  |  |
| 1 | ##### DG Yard | ##### 6.00 | ##### 6.00 |  |  |
| 2 | ##### Transformer Yard | ##### 4.00 | ##### 4.00 |  |  |
| 3 | ##### Car Parking | ##### 4.00 | ##### 5.00 |  | ##### 3 Nos. |
| 4 | ##### Dry Sludge/compost storage | ##### 10.00 | ##### 12.00 | # 6.00 | ##### 1 Nos. |

### All buildings shall be air conditioned unless agreed otherwise with the Engineer in liaison with the Employer. Finish floor level for all buildings except otherwise noted to be minimum 500mm above the surrounding finished walk way elevation. Unless specifically permitted or stated otherwise, buildings structures shall have a reinforced concrete base / floor slab, reinforced concrete frame, concrete block walls and reinforced concrete roof slab with edge parapets. Internal walls shall be of concrete block construction.

## 3.11.4.1 Design Criteria for Structures and Buildings

- Design Criteria for Water Retaining Structures.

- Requirements

All process units such as underground tanks, partly underground tanks and elevated tanks shall be water retaining structure and shall be water tight when subjected to external ground water and internal water pressures. Water retaining concrete structures shall comply with the following minimum requirements:

Design life:		50 years

Design code:		BS 8007 & BS 8110

Concrete grade:	OPC 40

Reinforcement cover:	shall be as per clause 3.8.2

All structures, whether liquid-holding or not, shall be designed such that they will not float or move when empty, because of groundwater buoyancy or any other reason. The structures shall be designed to counteract any possible floatation without the use of any type of groundwater pressure relief valves.

Concrete protection to surfaces in contact with sewage, sludge and gasses and sprays arising there from shall be provided as follows:

Class A: 3mm thick spray applied Methyl Methacrylate or Polyurethane.

Class B: Epoxy coating built up in layers to give a dry film thickness of 1mm.

Class C: Epoxy free resin coating followed by two coats of chemical and UV resistant polyurethane or methyl methacrylate resin to give a dry film thickness of 500 micron.

Table below details the level of concrete protection to be provided at key elements of the Works.

| Structure | Class |
| --- | --- |
| Inlet Works, Raw Sewage Storage Tank | A |
| Distribution Chambers and Channels , Tanks | A |
| Enclosed Chambers & Channels | A |
| Tertiary Treatment Plant – any enclosed area | B |
| Chlorine Contact Tank | B |
| All other external wetted surfaces | C |

- Surfaces in Contact with the Ground

Water retaining structures shall be tanked. A blinding concrete of 75mm along with 2 layers of tanking and 50mm thick tanking protection screed shall be provided for horizontal concrete surfaces. For vertical surfaces 2 layers of tanking with 12mm thick bitumen impregnated fibre board shall be provided as tanking protection.

- Testing of Water Retaining Structures

Watertightness shall be tested for water retaining structures including storage reservoirs and other miscellaneous structures that require to be watertight as per local/British standards.

- Design Criteria for Architectural Works for buildings

Hulhumalé STP is one of the Employer’s show pieces and the quality of architecture and building materials used shall reflect this.

- Windows and Doors

      - All Windows and doors shall be heavy duty industrial type and meet the requirements of the specifications.

      - The style of windows and doors shall be as per the Contractors approved architectural design.

      - Glass shall comply with the relevant provisions of BS 952.

      - Doors and windows frame shall be anodized marine aluminum.

      - Type of accessories and hardware shall be stainless steel 316.

      - Fully tempered laminated glass shall be used where glazing is required.

      - Fire rating shall be based on building location and use, to be detailed at design stage. The Contractor shall submit detailed drawings at construction stage for Engineer’s approval.

      - Exterior glazing shall be wind and watertight on completion.

- All external doors and windows shall be dust proof.

- All doors and windows shall be double glazed.

- Provide curtain vertical blinds for all the windows

- Doors and windows for SCADA room to be dust proof.

- Panic hardware shall be provided for all exist and emergency doors.

- All doors and buildings shall be provided with proper signage.

- Floor Finishes

The floor finishes shall be as indicated in the Table below.

| Building | Floor Finish |
| --- | --- |
| MCC Room | ##### Highly chemical resistant, hybrid polyurethane based, resin floor coating incorporating slip resistance grains |
| Pumping Station except Office Area |  |
| Walkway of Tanks and inlet Structures |  |
| Chemical Store |  |
| Administration Building | ##### Vitrified Tiles (600mmx600mm) with 100mm skirting |
| Security Building | ##### Ceramic Tiles with 100mm skirting |

- Walls:

The wall finishes shall be as indicated in the following table.

| Building | Finish Type |
| --- | --- |
| MCC Room | ##### Block work walls: painted plaster, 1 mist coat & 2 coats of washable acrylic co-polymer-based emulsion |
| Pumping Station Office Area |  |
| Chemical Store |  |
| Administration Building |  |
| Security Building |  |
| Toilets | ##### Ceramic Tiles |

The external wall finishes shall be weather proof exterior emulsion (water based 100% acrylic) to all plastered surfaces, concrete, exterior ceiling etc.

- Roofs:

All roofs shall be reinforced concrete unless specified. Water proofing, roof tiles and necessary roof rain water discharge facility shall be provided

- Ventilation

The Contractor shall provide adequate means of ventilation systems to buildings of the STP in accordance with the information contain herein, comply with the ASHRAE standard code of practice, or ASCE manual or equivalent, and recommendation of the local environmental and water authorities. Since the location of the STP is socially and ecologically sensitive the Contractor shall design the systems in such a manner that extracted foul air and noise generated from the machinery and equipment shall not create any kind of pollution, nuisance or disturbance to the eco system and neighbors around.

The mechanical ventilation systems shall be designed and installed to different areas of buildings according to the design requirement indicated in the table and if the design requirements are not covered in the below table Contractor can follow the codes mentioned above.

| Facility | Air Changes Per Hour |
| --- | --- |
| Small pump stations | 8 |
| Large pump stations. Higher air changes rate to be achieved by two speed motor fan or installation of two fans that shall be initiated by light switch | 12/20 |
| Dry Wells | 12 |
| Screening Area | 8 |
| Grit Removal Area | 8 |
| From Screen Covers | 10 |
| Sludge Building | 10 |
| Covered Tank | 0.5-1.0 OR 120% of the Maximum Filling Rate |

- Design Criteria Civil and Structural Works

- General

Unless specifically permitted or stated otherwise, buildings structures shall have a reinforced concrete base / floor slab, reinforced concrete frame, concrete block walls and reinforced concrete roof slab with edge parapets. Internal walls shall be of concrete block construction except at the first floor of Administration building which is gypsum board partition. The miscellaneous building details provide details of the finishes to walls and roofs shall conform to the Architectural specifications.

- Design Standards and Codes

All structural elements are to be designed in accordance with the applicable requirements and recommendations of the referenced codes and standards, to meet the specified performance.

- Structural Design-Water Retaining Structures

Water retaining concrete structures shall comply with the following minimum requirements:

Design life:		50 years

Design code:		BS 8007 & BS 8110

Concrete grade:	OPC 40

Reinforcement cover:	shall be as per specifications below

- Structural Design- Non-Water Retaining Structures

Non water retaining concrete structures shall comply with the following minimum requirements:

Design life:		50 years

Design code:		BS 8110

Concrete grade: 	OPC 40

Reinforcement cover:	shall be as per Clause 3.8.2

- Reinforcement Cover

As per Clause 3.8.2

3.11.4.2	List of Design Codes

| Number | Title |
| --- | --- |
| BS 6399-1:1996 | Loading for buildings. Code of practice for dead and imposed loads (AMD 13669) |
| BS 6399-2:1997 | Loading for buildings. Code of practice for wind loads (incorporating amendment No. 1 and corrigendum No. 1) (corrected and reprinted June 2002) |
| BS 8110-1:1997 | Structural use of concrete. Code of practice for design and construction (AMD 5917) (AMD 6276) (AMD 7583) (AMD 7973) |
| BS 4449:2005 | Steel for the reinforcement of concrete - Weldable reinforcing steel - Bar, coil and recoiled product - Specification |
| BS 8007:1987 | Code of practice for design of concrete structures for retaining aqueous liquids |
| BS 8004:1986 | Code of practice for foundations |
| BS 8666:2005 | Scheduling, dimensioning, bending and cutting of steel reinforcement for concrete - Specification (incorporating Amendment No.1) |
| CP 2012-1:1974 | Foundations for machinery. Foundations for reciprocating machines (AMD 1741) (AMD 1938) |

3.11.4.3	List of References

In addition to the above, the design guides / advice in following reference materials shall be used in the design.

| Number | Title |
| --- | --- |
| CIRIA R91 | Early-age thermal crack control in concrete. |
| Reynolds RC | Reynolds's Reinforced Concrete Designer's Handbook (10th Edition) |
| BS 6399-3:1988 | Loading for buildings. Code of practice for imposed roof loads (AMD 6033) (AMD 9187) (AMD 9452) |
| BS 5950-1:2000 | Structural use of steelwork in building. Code of practice for design - Rolled and welded sections (AMD Corrigendum 13199) (AMD 17137) (incorporating Corrigendum No. 2) |
| BS 5950-5:1998 | Structural use of steelwork in building. Code of practice for design of cold formed thin gauge sections (AMD 16502) |

3.11.4.4	Construction materials

Conventional reinforced concrete and structural steel work are used for the structure. The requirements of the materials are listed below.

- Soil Properties

Soil material properties shall be based on geotechnical investigation results.

- Structural Steel Works

Material Specification

| No. | Components |  | Specification | Strength (N/mm2) |
| --- | --- | --- | --- | --- |
| 1 | Hot Rolled | Beams | S275JR | 300 |
|  |  | Columns | S275JR | 300 |
| 2 | X-Bracing | Pipes | S275JR | 300 |
| 3 | High Strength Bolts | Grade 8.8 | BS EN 24014 and 24016 BS EN 24032,24033 and 24034 | 640 |
| 4 | Anchor Bolts | Grade 8.8 | BS 3692 : 1967 | 640 |

- Concrete

Concrete Coefficients and Constants

| Coefficients/Constants | Value |
| --- | --- |
| Reinforced Concrete, fcu | 40/20 N/mm² |
| Pre- Cast concrete, fcu | 40/20 N/mm² |
| Mass Concrete, fcu | 20 N/mm² |
| Pipeline protection and Chamber / Thrust blocks, fcu | 40 N/mm² |
| Concrete for Stone Pitching Bed, fcu | 25 N/mm² |
| Protection to tanking, fcu | 20 N/mm² |
| Blinding to Tanking, fcu | 20 N/mm² |
| Elastic modulus, Ec | 28,000 N/mm² |
| Concrete Density, c | 24.0 kN/m3 |
| Submerged Concrete Density, c | 14.0 kN/m3 |
| Density of block work | 22 kN/m3 |
| Coefficient of Thermal Expansion, α | 0.00001 |
| Uplift Factor of Safety | 1.2 |

- Concrete Mix

Concrete for structures (including water retaining structures and chambers) shall be Grade 40 manufactured with Ordinary Portland Cement. The aggregate size shall be 20mm and the minimum cement content shall be 370kg/m3. The maximum water/cement ratio shall be 0.42.

- Protection to Surfaces in Contact with the Ground

Water retaining structures shall be tanked. A blinding concrete of 75mm along with 2 layers of tanking and 50mm thick tanking protection screed shall be provided for horizontal concrete surfaces. For vertical surfaces 2 layers of tanking with 12mm thick bitumen impregnated fibre board shall be provided as tanking protection.

- Reinforcement

Reinforcement bars (epoxy, or epoxy coating on the most exposed surfaces of concrete) are to be in accordance with BS 4449: Specification for carbon steel bars for the reinforcement of concrete.  Welded wire fabric is to be in accordance with BS 4483: Specification for steel fabric for the reinforcement of concrete.  The following design strengths are to be used for the design of reinforcement:

Mild Steel	250 N/mm2 (BS4449) will be used as links

High Yield	460 N/mm2 (BS4449)

Safety factor for steel reinforcement strength will be 1.05 as per BS8110

3.11.4.5	Other Criteria

All other design criteria such as loading, loading combinations etc. shall be as per the relevant  Standards.

### 3.11.5.	Security and boundary fencing

### A boundary wall of 2.00m high and an entrance gate of 4.50m wide and a pedestrian access gate of 1.0m shall be provided.

### 3.11.6	Utilities, drainage, firefighting

- Storm Drainage:

A surface water drainage by gravity is to be provided for all paved surfaces. The drainage system shall be designed to receive a storm of 1 in 5-year return period of 20-minute duration. Site drainage system shall be connected to external storm water network or necessary outfall to the sea also to be provided.

- Wash water:

A municipal potable water supply connection is required from an adjacent tapping point. A sump of one day capacity will be provided at STP site and the sump shall be RCC/HDPE. A pressurized wash water ring main and wash water booster set shall be installed to serve the Works. Potable water shall be used for the wash water network.

Hose connection standpipes shall be provided within 30m of all areas requiring wash water for routine maintenance and cleaning. Each standpipe shall be capable of delivering a flow of at least 15l/s. The system design shall provide an operating pressure within the network of at least 30m head at all times, whilst delivering the peak flow for all process unit requirements and delivering 15 litres per second to any two standpipe locations. Pressure reducing valves shall be included for any specific plant items where a limited pressure head is required.

- Fire Protection System

The Contractor shall design, supply, install test and commission fire detection and suppression system. The fire detection systems shall be designed in accordance with NFPA 72 and all local requirements. Automatic fire suppression in all control panels, VFDs, soft starters and switchgears. Fire alarm and fire coating shall be provided for all cables under MCC rooms. Potable and mobile fire extinguishers in pump rooms, motor rooms, pipe gallery, MCC rooms, SCADA rooms, workshops, Admin building, odour control compound, screen house, blower rooms, chemical dosing rooms, chemical store, bulk store, laboratory, guard rooms etc. Firefighting system shall be provided for all the buildings. The water for firefighting system shall be used from TSE storage tank. The entire fire alarm system, fire protection system and firefighting system including all materials, components, equipment and accessories and their installation shall conform to the requirements of the local authority. Fire Alarm system shall have communication to Main SCADA system. All critical fire alarms shall be transmitted to main SCADA system.

### 3.11.7	Landscaping and parking

Landscaping involves beautification of Sewage Treatment Plant site by cultivating plants and trees of environmental value and suitably modifying the appearance of STP site. It shall add scenic value to the STP site to obtain maximum visual impact. Contractor has to develop proper landscaping in the STP site from professional Landscape Architect approved by employer.

A buffer zone around the periphery of the STP area shall be provided with planting tall trees. In addition to this the open area between the units also shall be suitably landscaped. Interlocking pavers of 600mm wide shall be provided around each unit. Shade parking shall be provided at the administrative building to accommodate 3 cars and two wheelers for the staff.

### 3.11.8	Diversion of Influent Sewer

The contractor shall study the existing pumping system of outfall 3 (New) and 2 and design/construct/ modify the wet well, pumps, piping, valves, and associated electrical and instrumentation equipment for forwarding the flows to the inlet works of the STP. The contractor shall utilize the existing mechanical/electrical/instrumentation equipment wherever required suitably which has further design life and make all functional to discharge the sewage to the inlet works. Provision to be made to dispose of the sewage to sea in case of emergency.

### 3.11.9	Suggested Ancillary STP units and Requirements

### In order to achieve the required quality criteria as per clause 1.2.1, the performance requirement of STP and based on the raw sewage characteristics (preliminary data analyzed by the consultant), it is suggested to propose a sewage treatment with the following process. This Process and Facilities description is intended to provide a general indication of the various unit processes and type of facilities that the Contractor shall be required to design, construct, and operate the STP with processes from families of technologies detailed in Section 1.21. b.

- Primary Treatment

- Secondary Treatment

- Tertiary Treatment

### 3.11.9.1 Preliminary Treatment

- Inlet Works:

Inlet Works shall be designed to receive flows and provide preliminary treatment as specified below. It shall comprise the following treatment elements:

- Flow Reception chamber/Stilling Chamber.

- Screening, Screenings Compaction and Dewatering

- Grit Removal.

- Flow Measurement.

- Oil and Grease Tank

- Flow Distribution Chamber

The channels and chambers of the Inlet Works are to be totally enclosed to provide odour containment. The atmosphere beneath the enclosure shall be vented through an odour control plant.

The design criteria given under each unit is the minimum criteria and if any additional data is required contractor has to consider the same and agree with the engineer during Proposal evaluation stage and detailed design stage.

- Flow Reception Chamber/Stilling Chamber:

For the STP where all or part of the influent flow is pumped through the outlet structure at outlet-1 (or 3) and outlet-2 locations, the Contractor shall connect the incoming line to the stilling chamber of the STP. Necessary isolation valves with actuators also to be provided as required.

The discharges from the pumping mains shall be designed to limit turbulence, and hence hydrogen sulphide release, to a minimum. Necessary bell mouth shall be provided to reduce velocity at the drop point. The flow reception chambers shall be designed to ensure that screenings and grit do not settle and accumulate. The receiving chamber is proposed to act as a receiving structure constructed out of reinforced concrete RCC C40 and will be constructed above the ground to avoid frequent pumping.

A bypass arrangement by providing necessary penstock with actuator shall be provided within the reception chamber. The sewage from the chamber flows to the downstream screen chamber. The flow reception chamber shall be supported on RCC columns.

Access stairways shall be provided at each end of the inlet works and elsewhere to access to all equipment. Walkway access with necessary handrail with removable chains wherever required shall be provided to all areas of plant and machinery requiring routing inspections, adjustments or maintenance.

- Design Criteria:

Design Flow = 22.50 MLD

No. of units = 1

Minimum Free Board (m) = 0.50

Width = Total width of coarse screen chamber

Length = As per design

Retention Time = 30 - 45sec.

- Screening, Screenings Compaction and Dewatering

- Fine Screens:

All incoming flows shall be screened. One Mechanical and One Manual fine screen shall be provided in the channel. RCC Platforms shall be provided at suitable level to enable operation and maintenance of the unit.

The Mechanical screens shall be either of the Step or Band /Escalator conforming to specifications and technical data sheets mentioned elsewhere. The screens shall have a maximum aperture of 6 mm in the two planes at 900to the flow direction. The Automated screens shall be designed to achieve a capture rate of at least 70% of particles greater than 6 mm in 2 dimensions.

The manual screens shall be made out of Stainless-Steel SS 316 flats 75mm wide and 10mm thick and these are welded to an outer SS frame and fixed to the channel. The openings shall be 10mm.

The following provisions shall be made in the design of the screenings system:

- Actuated penstocks shall be provided at each end of the screen channels to enable the channels to be isolated.

- A drain facility shall be provided in the floor of each screen channel. The drainage arrangement shall allow the contents of the channels to be discharged to the site sewerage system.

- One no. Manual Screen bypass channel shall be provided. Manual Screen should be sized to treat flow equivalent to the capacity of one Automated Screens. This by-pass channel shall be provided with Motor operated weir penstocks. A fixed bar screen with a clear spacing of 10 mm shall be provided and shall be arranged to allow screenings to be manually raked into a perforated drain tray positioned behind the screen.

- It shall be possible to bypass any single screen whilst keeping the remaining screens in operation.

- Depth control through the screens shall be provided by a free draining flow control device such as a flume.

- Screens and other equipment to be installed at the Inlet Works shall be provided with covers to limit the volume of air to be treated by the odour control facility.

- The screens shall operate fully automatic with differential type level control and timer control through a dedicated Inlet Works PLC. A Float type level switch for high level alarm also to be provided. Local panel with Start/Stop Push button stations shall be provided nearer to the Screen Channel location.

The screenings shall be conveyed to the screenings washing and dewatering plant either by launder channels, conveyor belts or screw conveyors. Each screen shall have a dedicated screenings transfer system and screenings washer compactor. The compacted screenings shall have a moisture content not exceeding 50% and a faecal matter content of less than 5% by weight. The screenings shall be arranged to discharge into skips fitted with removable covers and located at ground level. The spent wash water shall be returned to the flow upstream of the screens.

- Design Criteria:

Design Flow (Average Flow) = 10.00 MLD

Design Flow (Peak Flow) = 22.50 MLD

Number of Units = 1 Mechanical Working + 1 Manual Standby

Approach Velocity at Average Flow (m/sec.) > 0.3

Velocity through Screen at Average Flow (m/sec.) = 0.6 maximum

Velocity through Screen at Peak Flow and clear screen (m/sec) = 1.2 maximum

Velocity through Screen at Peak Flow and 50% clogging (m/sec) = 1.8 maximum

Free board u/s of screen (m) = 0.5 minimum

Minimum length of each screen channel shall be such as to have a minimum clearance of 1.5 Min front and 1.5 M on rear for easy access and control. A minimum length of 5 M will be preferred. The manual bar screen shall be fabricated from 75 mm x 10 mm thick SS flats with 10 mm clear opening. The assembly (SS bars and frames by using ISLC of suitable size) shall be installed in such a way that it can be installed and removed as and when required.

- Grit Removal

A grit removal facility shall be provided on the downstream of screen chamber. One Mechanical and One Manual grit removal facility shall be provided. Mechanical grit removal facility shall be of square type with a classifier mechanism and organic return pumps. Manual grit chamber shall be horizontal flow type and grit is removed by maintaining a constant upstream velocity of 0.30 m/sec by providing a Parshall flume (which also shall be used as flow measurement device) at the downstream of grit channel.

- Mechanical grit separator:

The grit separator shall be square in size and a compact grit plant consists of a Square Grit Settlement Chamber with scrapers, reciprocating type mechanical classifier, and organic return screw pump. One tapered Inlet channel running along one side with Deflectors for entry of sewage into the Grit Chamber. One tapered Outlet Channel for collecting the de-gritted sewage which shall overflow over a weir into the Outlet Channel. Actuated Sluice Gates of adequate size as per design shall be provided at the entrance and exit of the Grit Chamber. To enable easy operation of the Gates, RCC Platform with GI Railing shall be provided at the upper level.

A Central drive mechanism of worm reduction type driven through helical gear and motor or by geared motor shall be mounted on the RCC platform spanning the tank. All exposed steel parts shall be sand blasted and painted with epoxy. The walkway shall have RCC posts and handrails of stainless steel. All wetted parts shall be in mild steel with epoxy coating. The epoxy coating shall be suitable for corrosion as well as abrasion of the grit. The drive shall be provided with electro-mechanical device, torque indicating arrangement and mechanical trip contacts with electrical overload relays. Flow regulating vanes shall be provided at the inlet side of the collection chamber and shall be of FRP. The vanes shall be adjusted as per the flow requirement. The weirs at the outlet of grit chamber shall be SS 304 with minimum 3-mm thickness or FRP with minimum thickness of 6 mm. The spacing of anchor bolts of SS 316 for the fixing of the weir shall not be more than 450 mm.

- Classifier Mechanism:

The Classifier, during its reciprocating action, washes the grit and pushes it towards the upper delivery end of the classifier from where the washed grit is released on scrapers or trolleys for further disposal. In the reciprocating classifier, there are no movable parts under the sewage and thus there is very negligible wear of the components.

The Organic return pump returns the washed organic material from the grit back to the grit chamber and the same is kept in suspension and passed on further for treatment. Organic return pump will be located by the side of classifier so as to return organic back to the Degritting tank. The organic mixer will have specifically designed impellers to create washing action and a suitable motor through worm gear drive will drive the mixer.

- Manual grit separator:

The manual grit channel shall be designed as horizontal flow grit chamber by maintain a horizontal velocity of 0.30m/sec. Velocity is controlled by a Parshall flume on the downstream side. Grit is removed manually to a skip provided at the ground level. A drain pipe with necessary valve shall be provided to drain the channel completely.

- Design Criteria for Grit Removal Systems:

Design Flow (Average) = 10.00 MLD

Design Flow (Peak) = 22.50 MLD

Number of Units = 1 Mechanical Working + 1 Manual Standby

Size of grit particle =<20 mm

Specific gravity of grit = 2.65

Maximum Surface Overflow Rate = 960 m3/m2/day.

Hydraulic Retention Time = 60 -90 seconds

Freeboard = 0.50m (Min)

Side Water Depth = As per Design

Horizontal Velocity = 0.30 m/sec (Manual System)

Allowance for Grit Storage = 0.30m (Manual System)

Penstocks: Actuated penstocks shall be provided at the entrance and Exit to divert the flow between Manual and Mechanical grit removal system and u/s and downstream flow.

- Flow Measurement

The flow measurement shall be by Parshall Flumes which will also act as a velocity control device for grit chamber. There will be an approach channel, a throat, and a downstream channel. At the throat, there will be a hydraulic jump and a corresponding head loss. An Ultra sonic flow meter shall also be provided for flow measurement shall be mounted above the channel to measure the flow. Parshall flume shall be designed as per International Standards.Total flow measurements shall be recorded for all types of flow measurement. An integrator shall be provided to enable the returned flows to be deducted from the incoming flows to the Inlet Works such that a true record of the treatment flow is produced.

- Oil and Grease Tank

The Oil and Grease tank is a pre-treatment unit which proposed to remove fats, Oil and foam from the waste water. High levels of Fats, Oil and Grease inhibit the biological processes. A semi perforated pipe shall be fixed at the downstream baffle to remove the freely floating oil easily. As the Oil and Grease trap is located at the downstream of the grit channel, the grit settled in the bottom of the tank will be less. However, any grit settled at the bottom can be removed by a portable grit pump.

- Design Criteria for Oil and Grease Trap:

Design Flow (Average) = 10.00 MLD

Design Flow (Peak) = 22.50 MLD

Number of Units = 1

Residence time in the trap = 3-15 minutes at peak flow.

Additional Requirement = Baffle wall shall be provided at one third distance from inlet and outlet of the tank. Inlet and outlet Tee also shall be provided.

Freeboard = 0.50m (Min)

Material of Construction = RCC channel supported on columns. The oil shall be collected in a trough and periodically removed by gravity for disposal.

- Flow Distribution Chamber

Flow distribution to the secondary treatment stage shall be by means of discharge pipes having free discharges. The flow distribution shall be designed for peak flows and the works return flows. Provision shall be included to allow flows to be split equally into the number of streams to be provided. The distribution chamber shall include the facility to isolate the flow to a Secondary Treatment stream. Provision shall be included in the design to enable the feed lines to the isolated stream to be emptied either by free draining to the Secondary Treatment stage or by the flow being discharged to the site drainage system.

Necessary Flow distribution arrangements such as weirs, Gates with necessary arrangements etc. shall be provided within the Chamber. If one stream is isolated the rest of the stream should be able to handle forward the flows. Provision in term of hydraulics levels will also be made in order to handle flows if one biological process is under maintenance.

      - Secondary Treatment – Biological Treatment

- Treatment Process:

Secondary treatment processes included but not limited to the following options shall be considered for organic removal along with Biological Nutrient Removal (BNR) to achieve the treated sewage quality specified in section 1.2.1

- Extended Aeration Process (EA)

- A2O Process (without coagulant dosing system)

- Bardenpho  4-stage Process (without coagulant dosing)

- Modified Ludzack Ettinger (MLE) Process (without coagulant dosing system)

- Sequential Batch Reactor (SBR) (with Anoxic Tank)

- Moving Bed Bio-reactor (MBBR) (with Anoxic tank)

Please note that multi-stacking of units on one another, in any treatment technology, shall not be acceptable. All the units should be on the ground floor which can be accommodated in a building unit except Air Blower Room/MCC/Laboratory cum Administration, UPS room, Manager’s room (G+1) unit and Centrifuge building.

- General:

Following are the general and minimum requirements and any specific requirements required to satisfy the treated effluent standards, shall be deemed to be included in the detailed design.

- The secondary treatment stage shall receive the screened and de-gritted sewage. There shall be no primary settlement stage.

- The Plant shall be complete with all air blowers, Return Activated Sludge (RAS) pumps (based on treatment process), Surplus Activated Sludge (SAS) pumps, decanting equipment (based on treatment process), control and monitoring equipment, pipework and fittings, and shall operate automatically under normal operation.

- All isolating valves on influent and effluent pipes and any cross-connecting pipe work shall be electrically operated. All isolating valves on sludge pipelines shall be electrically actuated.

- A minimum freeboard of 500 mm shall be provided above the tank’s normal operating top water levels at the peak design flow.

- The Secondary Treatment process shall be designed to achieve the required effluent discharge consent in terms of Ammoniacal and Total Nitrogen by biological means. Nutrient Removal should be maximised by Biological Process.

- Aeration shall be achieved using Jet Aerator, Mixer Aerators or Fine Bubble Diffused air system (Ceramic diffusers shall not be used). Equipment shall be suitable for any chemical cleaning system recommended by the diffuser manufacturer.

- A tertiary treatment also required to be included in order to get the effluent quality mentioned elsewhere in the document.

Biological Process Requirements:

| Biological Process - Design Requirements |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Treatment Process | ##### SRT (d) | F/M (Kg BOD / Kg MLVSS-D) | MLSS (mg/L) | Aeration Tank HRT (hr) | RAS (% of influent) |
| Extended Aeration (EA) | ##### 10-26 | ##### 0.10-0.18 | ##### 3000-5000 | ##### 12-36 | ##### 0.25-1.00 |
| MBBR | ##### Designed based on 0.8 – 1.2 Kg BOD / m3.d |  |  |  |  |
|  | ##### Minimum HRT of 5 Hours |  |  |  |  |
|  | ##### Volume of MBBR Media – Min. 33% and Max. 50% |  |  |  |  |
| SBR – Continuous Flow and Intermittent Decant | ##### 15-20 | ##### 0.05-0.08 | ##### 3000-4000 | ##### Min 21hrs (without Anoxic / Selector Zone) | ##### As per Bidders Design |
| SBR – Intermittent Flow and Intermittent Decant | ##### 4-20 | ##### 0.05-0.3 | ##### 3500-5000 | ##### Min 21 hrs(without Anoxic / Selector Zone) |  |

- Aeration Basins:

Generally, Extended Aeration Process is preferred for the STP if the capacity is less than 10 MLD. For nutrient removal, coagulant dosing system for phosphorus removal and/ or tertiary treatment by filtration shall be opted, wherever applicable. Biological Nutrient Removal is preferred and it shall be by any of the process mentioned above. Necessary Anaerobic/Anoxic Zones shall be constructed as per requirement and the flow from these tanks to the downstream Aerobic tank shall be by gravity. Necessary Mixers/ mixing arrangements in the above tanks shall be provided as per the bidder’s design.

The top-of-wall of aeration basins elevation shall be such that system should work on a gravity influent condition. No Equalization Tanks or flash filling are acceptable. There shall be minimum two Aeration tanks for flexibility.

Each aerobic basin shall have a separate diffuser grid supplied by a separate air drop pipe with the air flow controlled by a separate valve and measured by a separate flow meter. All systems shall use Dissolved Oxygen with VFD driven Blower.

The blowers that are to provide aeration to the tanks shall be housed within a building. The layout of the building shall allow for the additional blowers required for other process such as Aerobic Sludge holding tanks Aeration etc. as suggested by the bidder. Each Aeration tank has its own duty and standby air blowers.

The RAS piping/channelling shall also be designed such that potential future piping and valve modifications necessary to match the potential future zone modifications described above can be accomplished with ease and minimal disruption. Mechanical surface aerators are not acceptable. In case of any other type of Aeration Equipment one total set of the equipment should be provided as standby. Diffused aeration shall be of retrievable type.

The aeration shall be provided primarily for biological treatment. The aeration equipment shall also to provide adequate mixing arrangement in the aeration tank to keep the solids in suspension. For diffused aeration, the air volume for mixing shall be not less than 1.8-2.7 m3/hr/m2 of floor area.

- SBR Basins:

SBR process shall be designed to treat sewage for organic load reduction along with biological nitrification-denitrification and biological phosphorus removal. SBR designs shall strictly comply with the minimum sizing and all other requirements specified in the Proposal documents.

Each SBR basin shall have a separate diffuser grid supplied by a separate air drop pipe with the air flow controlled by a separate valve and measured by a separate flow meter. All systems shall use Dissolved Oxygen with VFD driven Blower. The blowers that are to provide aeration to the tanks shall be housed within a building. The layout of the building shall allow for the additional blowers required for other process such as Aerobic Sludge holding tanks Aeration etc. as suggested by the bidder. Each SBR tank has its own duty and standby air blowers. The discharge from any given blower shall be routed to not more than a single SBR basin at any given time. Diffused aeration shall be of retrievable type.

For SBR process, the recirculation of activated sludge (RAS) may or may not be provided depending upon bidder’s design/proposal. No. of WAS (waste activated sludge) pumps shall be minimum 1W+1S for each basin.

The effluent decanting arrangement and operation shall be designed to include a proven, robust and effective manner of decanting top-waters with a proven history of satisfactory performance on similar sized installations. The design and proposed operation of the Works shall ensure that foam, scum, oils fats and grease are not discharged with the effluent from the secondary treatment stage.

The rate and method of decanting shall ensure that no scouring or re-suspension of the sludge blanket shall occur. Decant mechanisms shall be fixed or mechanically driven. Floating decanters shall not be permitted. Decanter components in contact with the liquid shall be stainless steel. The design of the decant mechanism shall permit a visual inspection of the discharge and the identification of any leakage within the decant mechanism. The effluent decanter shall be designed to include a proven, robust and effective manner of decanting top-waters with a proven history of satisfactory performance on similar sized installations.

- MBBR Basins

The bioreactor shall be designed to treat the peak flow sewage for organic load reduction along with BNR using an integrated fixed Film Activated Sludge system using free floating/moving cylindrical biomass carriers having more than 7years of life. The media/carriers shall be kept in suspension at any time by diffused aeration. MBBR tanks shall be aerobic stage for BOD removal and Nitrification. Necessary biological process shall be adopted for the removal of nutrients.

The recirculation of activated sludge (RAS) may be provided depending upon bidder’s design/proposal. The MBBR bio reactor shall be suitably sized to achieve the desired treated sewage quality. The shape of the reactor can be circular or Square or rectangular as per the bidder’s design, the shape should be so fixed so that it is suited for a compact and operationally flexible layout.

Reactor Media shall be as per bidder’s patented design but compatible with other media types for future operations considering about 20% variation in specific surface area. The media shall have a specific gravity of equal to or less than that of the waste water and be suitable of providing axial rotation in all planes as well as ensuring aeration to all surfaces. Aeration should be done through fine or coarse bubble diffusers.

Media Trap made from SS 316 (wedge wire screens) or superior material as approved by Employer shall be provided to ensure that media does not escape to the downstream unit. The size of the screens will be governed by the size of the bio-carriers.  The entry and exit of waste water shall be at opposite ends both in horizontal &vertical plane. The reactor dimensions, media quantity shall be adequate for providing adequate surface area for maintaining the biomass required for degradation and air required as required to achieve the quality. The aeration system shall be provided for sufficient oxygen supply for the effective biodegradation in aerobic reactors. The level of dissolved oxygen in the Aerobic reactors shall be maintained minimum at 2.0 mg/l or above to facilitate the required biodegradation.

Blowers, piping, valves and other equipment to maintain air flow to the aerobic reactors must suit the needs of the media circulation and aeration of MBBR system. Each MBBR tank shall have a separate Duty and Standby blower as per process requirements. All systems and process equipment as necessary to meet the performance requirements will be provided by the Contractor.

- Secondary Clarifiers

For STPs other than SBRs, secondary clarifiers shall be provided to separate mixed liquor solids from the treated liquid phase. Plate/Tube settler clarifier for Secondary Clarification shall be designed and constructed be as per international standards and as per manufacturers recommendations.

- Air Pipe work

- All air pipework shall be stainless steel suitable grade in accordance with the latest specifications mentioned elsewhere.

- The air flow to each process stream unit shall be individually controlled and shall be independent of the other units. The air flow to each zone within the unit shall be independent of the other zones and other tanks.

- Plug valves shall be installed in individual headers and in each individual drop-down pipe, to control the volume of air along the pipes.

- Lateral pipe work shall be securely fixed to the tank floor using fixings that allows at least ± 50 mm vertical adjustment. All diffusers shall be levelled across the entire plant to a common datum to ensure equal immersion depth. The maximum allowed deviation from this datum shall be ± 5 mm to ensure even air distribution. Where separate systems of diffusers are fed via independent bus mains, each system may be levelled to an independent datum, to within the same tolerance.

- Lateral pipe work shall be jointed (e.g. welded) and fixed to prevent an individual pipe or fitting from lifting or turning, causing diffusers to move out of position.

- If periodic chemical cleaning is a procedure required to maintain the efficiency of the diffusers, self-sealing hose connection points shall be provided for the purpose. At least one connection per aeration zone shall be provided.

- Control valves shall be of the eccentric plug type giving a linear characteristic of air flow against the degree of opening. Each valve shall be supplied with a pressure/flow calibration certificate.

- Control valves shall be motorized and be suitable for a continuously modulating duty. They shall be fitted with a position feedback signal derived from a non-contacting transducer. All valves shall be lockable in any position.

- Butterfly type isolating valves shall be fitted in each individual treatment zone or pocket. They shall not perform any control function.

- Suitable tapping and air flow measuring devices shall be installed on each aeration zone. Each tapping shall be clear of any flow disturbing equipment and be safely accessible from walkways or platforms. Tapping shall be suitable to receive a portable hot wire anemometer calibrated to read standard cubic metres per hour. The Contractor shall supply one set of indicating instruments for each aeration zone of one process stream. A permanent flow measuring device in the air bus main of each aeration module shall be installed.

- Diffusers

- The diffusers to be provided shall be EPDM membrane type diffusers with a permanent temperature resistance of 1400C and a minimum tensile strength of 11MPA when measured in accordance with DIN 53504 S11. Diffusers shall have a proven track record of successful and efficient operation in a sewage works aeration plant.

- Diffusers shall be fully interchangeable and shall produce fine bubbles in the range 1 to 5 mm nominal diameter. They shall be capable of operating over a range of air flows with a turn down ratio of 5:1. Diffusers shall be self-sealing when the air supply is isolated.

- Each diffuser shall be securely fastened to a purpose designed base plate by a peripheral retaining ring with O-ring or C seals. The base plate assembly and retaining ring shall be of uPVC. Bolted assemblies shall not be used.

- The diffuser/base plate assembly shall incorporate a suitable orifice for control of air flow and shall be securely fixed to the pipework system to ensure the assembly remains in position under all operational conditions and during manual in-situ washing (low pressure hosing). The number of diffusers per zone shall be determined by the Contractor to satisfy the flows detailed in the Particular Specification and the requirements of the oxygen efficiency test. Diffusers shall be evenly distributed within the whole floor area of each zone to prevent dead areas and shall be within the range of 3% to 15% diffuser area per square metre of floor area.

- Should the design require areas to be aerated using coarse bubble aeration, aerators shall be in accordance with the Specification mentioned elsewhere.

- The Contractor shall supply all supporting design calculations and criteria used to determine the type, size and number of aeration devices selected.

- Return and Surplus Activated Sludge Pumping

The rate of Return Activated Sludge (RAS)(if applicable) and Surplus Activated Sludge (SAS) shall be measured by electromagnetic flow meters installed on the pipelines.

      - Tertiary Treatment

The secondary treated sewage shall produce an effluent quality of BOD: TSS: TN of 10:10:10 standards. Tertiary treatment of effluent involves a series of additional steps after secondary treatment to further reduce organics, turbidity, nitrogen and pathogens. The suggested tertiary treatment processes included are Disc Filters and Chlorination system for disinfection in order to meet the standards. However, the contractor is free to provide his own methods to meet the standards specified in section 1.2.1.

- Disc Filter

The secondary treated sewage is allowed to pass through Disc filter located in an RCC tank. The size of the tank will be as per vendor’s requirement. It consists of several discs mounted vertically in the tank. Operationally, treated sewage flows by gravity from the exterior of the disc through the filter medium and the filtered water is collected through the centre drum to the treated sewage collection side of the RCC tank. During the filtration process, loss of head gradually gets higher as suspended solids are trapped on the filter media. This raises the water level in the tank and activates the water level sensor to rotate the disc and start the suction cleaning pump to clean automatically. Disc filter shall be 100% submerged in the RCC tank. An effluent turbidity up to 2 NTU can be expected after filtration.

Design Criteria For Disc Filter:

| Disc Filter |  |
| --- | --- |
| Description | ##### Design Criteria |
| Design Flow | ##### 10, 000 m3/day (Average Flow) |
| No. of units | ##### 2 no. (or as suggested by the manufacturer) |
| Typical Hydraulic Loading Rate (HLR) | ##### 0.08 – 0.2 m3/m2.min |
| Peak HLR | ##### 0.26 m3/m2.min |
| Submergence | ##### 100% |

- Disinfection

Chlorine Contact Tanks shall be provided for disinfection of treated sewage from the secondary treatment as per design. Chlorine shall be injected via an inline vacuum educator placed in the biologically treated sewage pipe just upstream of the Chlorine Contact Tanks or through diffusers in Chlorine Contact Tank. Since the STP capacity is above 5 MLD capacity, Gas chlorinator is preferred.

A Chlorination Building shall be provided to house all chlorination equipment including chlorine cylinders, chlorinators, and all associated equipment.

- Chlorination System

The objective of chlorination of water is to reduce organic matter, algae growth and to remove pathogens etc. One no. chlorine contact tank with necessary baffles shall be provided for the disinfection of treated sewage. The chlorine shall be dosed in the chlorine contact tank through diffusers.

Chlorination building is proposed to accommodate Chlorinators consist of tonner manifold, automatic gas feeder, vacuum regulator, pressure reducing valve, vacuum relief valve, controller and ejector. Chlorine is withdrawn from the tonners and is conveyed to vacuum regulator. Thereafter chlorine is conveyed to chlorinator. The required vacuum is created and pumping water under pressure to the injector assembly with the help of 2 Nos. (1W+1S) booster pumps for each chlorinator. The chlorine gas is then mixed with water in the injector and the chlorine solution thus formed is dosed to respective dosing point through diffusers. Adjacent to the chlorine contact tanks a chlorination house shall be provided to house the service water pumps, filter backwash pump and air scouring blowers. Chlorination building shall be provided material handling equipment like EOT crane etc. A complete Chlorination system with necessary safety accessory and controls shall be provided as per standards. A pit and absorption system shall be provided to contain and neutralise chlorine in the event of a leak.

Design Criteria:

| Chlorine Contact Tank (CCT) |  |
| --- | --- |
| Description | ##### Design Criteria |
| Design Flow | ##### Rate of decant flow to be considered |
| No. of units | ##### 1 no. |
| Retention Time | ##### 30 mins |
| Others | ##### Chlorinator, Chlorination building to house 4 weeks chlorine drums, necessary service pumps etc. to be provided |

- Emergency Outfall

An emergency gravity outfall from the chlorine contact tank to the sea nearer to the STP site shall be provided with necessary valve arrangement. This shall be operated during emergency period in case the pumping system is under maintenance.

      - Sludge Handling, Treatment and Disposal

The sludge treatment shall include Biological Sludge sump, sludge dewatering facility and dewatered sludge storage (emergency) and In Vessel Composting.

- Biological Sludge Sump

All Surplus activated sludge from the Secondary Treatment process shall be discharged to the Sludge sump.  Air agitation requirement of 1m3/hr/m3 of sludge volume shall be provided by a blower. The air flow to the tank shall be automatically adjustable to ensure that the minimum agitation levels are achieved. The blower shall be working one duty and one standby arrangement. The blowers that are to provide aeration to the Biological Sludge Sump shall be housed within a building.

The air main from the blower room to the biological sludge sump shall be above ground and shall provide adequate clearance beneath for site, construction and operational vehicles. The air mains shall be constructed of stainless-steel grade 316 S33 to BS 970-1. Outdoor sections of the air main(s) shall be supported on plinths with bolted pipe straps. Surplus activated sludge pumps shall be one duty and one standby arrangement.

Centrifuge feed pump shall be progressive cavity type with one working and one standby arrangement and the detailed specifications will be presented elsewhere in the document.

- Sludge Dewatering

Sludge shall be mechanically dewatered using centrifuges. Two no. Centrifuges shall be proposed (1 Duty + 1 duty assist) configuration and material of construction shall be as per detailed specifications. The sludge shall be dewatered to achieve 22-25% dry solids as detailed in below Table. The filtrate from the centrifuge shall be collected in a slump and return the filtrate to the inlet works.

Table: Sludge Dewatering Requirements

| Parameter | Requirement |
| --- | --- |
| Minimum no. of units to be installed | ##### 2 No. (1 Duty and 1 Standby) |
| Dry Solids to be achieved | ##### 25% dry solids, 95% Compliance |
| Solids capture ratio | ##### Minimum 95% Compliance |
| Quantity of Polymer | ##### Maximum 2.5Kg/Ton dry solids, 95% Compliance |
| Polymer Dosing and preparation Tank | ##### 1 Duty/1 Standby |
| Polymer Dosing Pump* | ##### 1 Dedicated pump per Centrifuge |

*- Suitable piping arrangement to be made so that any dosing pump can feed any Centrifuge.

The number of dewatering units, and associated pumps and polymer preparation units, to be installed in this contract shall be 1 duty plus 1 standby working 12 operating hours per day and 7 days per week.

The dewatering plant shall be housed in a building complete with all services. The ground floor is of sufficient height in order to discharge the dewatered sludge directly into a tipper. The dewatering equipment shall be close covered with air extracted to an odour control unit. Air extraction rates shall be sufficient to prevent odorous air escaping from the covers.

Polymer Preparation mixing equipment shall be provided. One dedicated dosing pump will be provided for each Decanter Centrifuge. The mixing system shall provide all necessary connections and isolating valves for the potable water. The Contractor shall operate the plant using potable water for mixing.

A separate polymer/chemical store room shall be provided within the dewatering building. The storeroom shall provide space to store sufficient chemicals and other raw materials for up to 30 days operation of the dewatering equipment. The storage volumes shall be based on the estimated chemical usage to dewater the design sludge associated with the design flows and loads. The environment within the chemical store shall be designed to maximize the effectiveness of the chemical, and to minimize the adverse effects due to storage. Provision shall be included for the containment of leakages of chemicals and for the protection of surfaces that may be affected by any leakage. Surfaces to be protected from chemical spillage and shall be protected by epoxy coating or other materials resistant to the chemicals that may be spilled. Paved access shall be provided to the building to allow for deliveries and for access and maintenance purposes. Lifting facilities shall be provided to enable off-loading of supplies and equipment and for the operation and maintenance of the equipment. An overhead crane shall be provided to allow for the maintenance of the centrifuges. The crane shall have a Safe Working Load of 2,000 kg, or 50% above the heaviest item to be lifted, whichever is the greater. Provision shall be included to allow areas requiring washing down to be drained and the resultant flows to be returned to the site drainage system where appropriate.

A control room shall be provided within the dewatering building to provide a clean environment for all local control panels. The control room shall be air conditioned by split unit air conditioners.

An external emergency stainless steel eyewash and emergency deluge shower shall be provided using potable water.

- Dewatered Sludge Handling

Provision shall be included for 2no. of tipper trailer and the dewatered sludge to be  discharged directly to the feed bunkers located within the In- Vessel compost equipment area. The following minimum equipment shall be provided to allow the movement of sludge from the site.

- 1 No. wheeled loader complete with trailer towing hook.

- 2 No. tipping trailer

The wheeled loader shall be a new diesel powered, two-wheel steer, rubber tyred unit with high lift hydraulically operated loading arm and bucket. The loader shall be fitted with a towing connection for the trailer truck. It shall be from a well-recognized manufacturer such that spare parts shall be readily available within Maldives.

- Emergency Sludge storage Tank

An emergency sludge storage tank of minimum 3 days shall also be provided. The emergency tank shall be a covered RCC tank with necessary openings for the removal of sludge.

- In Vessel Composting and Compost storage Area

It shall be noted that the entire daily production of the sludge could not be used for gardening etc and a substantial portion of the compost may have to be stored or disposed of in the Employer  designated  island-based  storage area. Thus, the Contractor shall negotiate with the  solid waste disposal agency WAMCO  for either WAMCO to transport and dispose of the remaining compost sludge  in the Employer nominated area or  WAMCO to find potential  buyers (farmers or resort islands)  to use the sludge compost as fertilizers.

      - Odour Control

The odour control unit(s) (OCU) may be a single central unit or a number of units located locally to the odour source. OCUs shall be designed with the fans on the outlet end, drawing air through the unit. The Contractor shall design the Works to minimise turbulence and the release of hydrogen sulphide and other odorous compounds.  Transitions shall be smooth and free drops shall be avoided unless essential for the process or hydraulic design.

Confined spaces that require routine access shall be ventilated at twelve air changes per hour.  Confined spaces that do not normally require access but contain sewer gasses shall be ventilated at a rate of six air changes per hour.

Covers to areas that require odour control shall be a marine quality aluminium of suitable grade for the atmosphere that will be encountered below the cover.  Covers that are to be walked upon shall be designed to take a distributed load of 750kg/m2 and a drop load of 50kg from 1m.  Covers that are not designed to be walked on shall have handrails to prevent unauthorised access and warning signs stating that the covers are not designed for man access.  Covers shall be easily removed to gain access to the areas below them requiring maintenance.

The objective of the odour treatment plant for the proposed STP is to treat the odourous air from the wastewater, biosolids treatment processes at the plant and to achieve almost zero odour nuisance in the adjoining areas of the STP. Thus, the treatment will be sufficient degree to mitigate any potential nuisance in the surrounding environment.

The design shall include a two-stage scrubbing unit designed to treat the foul air comprising of a biological system such as bio trickling filter followed by Activated Carbon Filter. The Activated Carbon Filter will act as a polishing unit only. The inlet concentration of H2S shall be 500ppm (Peak) and the outlet shall be 99% removal. All the mechanical and electrical equipment including control panel H2S analyzer to be included. A dedicated water supply line shall be provided for the supply of potable water to the bio trickling filter.

### 3.11.10	Design Deliverables

A. 	Design Submissions

The Contractor shall submit details of the proposed design for approval as mentioned below. The Contractor shall ensure that drawings, calculations and schedules are adequately checked and amended before submission to the Engineer.

The Contractor shall submit all reports, drawings and documents in hard copy and in electronic format using software that is compatible with the Employer’s computer systems. Design calculations must be submitted in their original electronic file format (e.g. Excel). All documents shall be produced in digital format compatible with the latest version of Microsoft Office. The main text for reports shall be Arial 11.

Hard copies of reports (7 copies) shall be comb bound with hard covers with accompanying drawings up to A3 size bound in. Drawings larger than A3 size shall be folded and inserted into plastic folders.

B. 	Detailed Design Stage

The contractor shall review the information available for the design of the Works and shall confirm the adequacy of the information available to proceed with the design. If the Contractor considers that additional information or surveys are required to verify or supplement the available information the Contractor shall carry out the necessary investigations or surveys as appropriate. The costs and time involved in undertaking surveys investigations and reports shall be deemed to be included in the Contractor’s tender submission.

The Detailed Design Report (DDR) shall confirm and develop the information provided within the Contractor’s tender submission. Raw sewage sampling data is available in Clause 1.4 of Part-The Contractor is advised to carry out raw sewage samples and confirm the raw sewage sampling data is adequate to carry out the process design and will be able to get the effluent standards as provided in the section 1.2.1. The information shall be provided in sufficient detail to satisfy the Engineer that the proposals will meet the Employer’s requirements such that approval to proceed to the construction stage can be granted. Any detailed design work carried out in advance of the Engineers written approval to proceed with the construction stage will be entirely at the Contractor’s risk. The Contractor will not be entitled to any costs incurred due to any abortive work arising from the commencement of the construction in advance of the Engineer’s written approval to commence this stage of the work.

The Contractor shall submit copies of design calculations, schedules, and drawings to the Engineer for acceptance, as detailed below:

- General layout drawings for the works;

- General arrangement and elevation drawings of the plant and structures;

- Structural drawings, schedules and calculations for all structures;

- General arrangement and elevation drawings of buildings;

- Superstructure and fabricated metalwork fabrication drawings and calculations;

- Pipeline layouts, longitudinal sections and calculations;

- Pipeline connection details;

- Process calculations;

- Hydraulic profile drawings and calculations;

- Detailed Odour control system report

Function diagrams for the following

- Plant performance curves

- Electrical Wiring and Schematic Diagrams and Calculations; Single Line Diagrams

- Process control, Instrumentation, SCADA & PLC system Architecture drawings an detailed interconnection diagrams;

- Cable schedules and routing diagrams;

- Routing diagrams for all services;

- Internal and Emergency lighting arrangements with level of illumination

- Site lighting arrangement with levels of illumination;

- Street lighting arrangement with levels of illumination

- Road and footpath layout;

- Road drainage layout and calculations;

- Architectural drawings for buildings and boundary walls.

- Hard and soft landscaping drawings

- Any other drawings or calculations that the Engineer may require to fully illustrate the Contractor’s proposals

C. 	Engineering Report

Following completion of the design of all the elements of the Works for which the Contractor shall be responsible, the Contractor shall produce an Engineering Report.

The Engineering Report shall summarize the work for which detail design has been undertaken. The report shall include sections on the design criteria, process, hydraulic, structural and electrical calculations and shall summarize the major items of M & E equipment together with equipment capacities. Calculations shall be included in an Appendix. Drawings shall be prepared on AutoCAD and shall be reduced to A3 size and bound.

# 4.	Planning, design, approvals and documents

## 4.1.	General

With respect to the planning and design of the Works, the Contractor shall:

- ensure that the Works is designed to comply with the specifications included in these Employer’s Requirements and the standards of performance included in the Schedule of Performance Standards.

- ensure that its designs are in accordance with the design codes and standards specified in Section 11 of the Employer’s Requirements or where not so specified, in accordance with good engineering practice;

- Design the Works to minimize adverse environmental impacts;

- meet all the obligations under the prevailing environmental regulations and the Environmental Management Plan;

- Unless otherwise agreed with, or directed by, the Employer’s Representative the Contractor’s Design shall be consistent with the Contractor’s Technical Proposal.

## 4.2.	The Environmental Management Plan

Refer to Appendix 1 of Employers Requirement

## 4.3.	Permits and approvals (requirements)

All permits and approvals will be facilitated by the Client upon request.

## 4.4.	Initial site investigations and studies

The site is a barren land without any existing utilities. It comprises a land parcel of about 6475.6sqm for STP and another adjoining land parcel of land of about 1700sqm is allocated for In-Vessel Composting Plant. The existing ground level is approximately 1.95m above datum. The contractor shall carryout a topographic survey of the land and geotechnical investigations of minimum 6 no. of bore holes within the area in order to develop the structural design.

In addition to this, the Contractor shall carry out necessary topographical survey and geotechnical investigations along the alignment which he proposes to adopt for the influent sewer line (sewage diversion mains) and for conveying the treated effluent outfall line to the existing outfalls.

4.5	Durability of the Works

The Contractor shall design the Works to meet or exceed the minimum asset lives shown in the asset life table below.

| Description | Design life (years) |
| --- | --- |
| Water and wastewater pipelines | 50 |
| Civil and structural works | 50 |
| Building works (administration, ablution, laboratory, workshop, store) | 50 |
| Roads and infrastructure work | 10 |
| Steelwork | 30 |
| Pumps and mechanical equipment | 20 |
| Equipment for chemical precipitation and polymer preparation | 20 |
| Switchgear, transformers, internal cabling, heavy electrical equipment | 20 |
| Instrumentation and control | 10 |
| Emergency generator | 20 |

The Contractor shall develop and submit to the Employer’s Representative for approval, a durability plan (The Durability Plan) which will demonstrate how its design will meet the specified asset lives. The Durability Plan shall include:

- An analysis of the nature of the Works environment and the main durability issues to be addressed;

- Specifications for concrete and reinforced concrete structures including proposed concrete specifications, crack width limits, concrete cover provisions, use of epoxy coated or stainless-steel reinforcement bars, and use of proprietary concrete surface coatings and treatments;

- Specifications for steel and stainless steel used in civil and building structures and specifications relating the use of galvanized or other coatings;

- Specifications for ancillary structures such as walkways, handrails, and stairways;

- Specifications for critical mechanical and electrical plant and equipment;

- Specifications relating to buildings and architectural features.

4.6	Contractors Documents (Design-Build) and progress reports

### 4.6.1.	Submission and approval of Contractor’s Documents (Design-build)

The Contractor shall prepare the following Contractor’s Documents for the Design-Build for review only, review and approval, or review and consent by the Employer’s Representative.

If no submission date is specified, the submission dates shall be in accordance with the Contractor’s time programme, prepared pursuant to GC 8.3.

Contractor’s Documents (design-build)

| Report/deliverable | Deadline for Submission | ER review only, ER review and approval, or ER review and consent1 | Nr of copies to be supplied (see GC 1.9) |
| --- | --- | --- | --- |
| Contractor’s Programme (see GC 8.3) | As GC 8.3 | Review & approval | 3 hard copies and 2no. soft copies |
| Initial site surveys | ##### Within 4 weeks after site possession | ##### Within 2 weeks after submission | ##### 3 hard copies and 2no. soft copies |
| Project Specific Quality Assurance Plan (Design Build) | Within 2 weeks from the date of commencement | Within 2 weeks after submission |  |
| Health and safety plan (Design-Build) | Within 2 weeks from the date of commencement | Within 2 weeks after submission |  |
| Durability Plan | Within 2 weeks from the date of commencement | Within 2 weeks after submission |  |
| Design Report | Within 8 weeks from the date of commencement | Within 4 weeks after submission |  |
| Preliminary design drawings | Within 8 weeks from the date of commencement | Within 2 weeks after submission |  |
| Construction drawings | Within 10 weeks from the date of commencement | Within 2 weeks after submission |  |
| As-built drawings | As GCC 5.5 | As GCC 5.5 | 3 hard copies and 2no. soft copies |
| Plan for the Tests on Completion of Design Build Etc. |  |  |  |
| O&M Manuals | As GCC 5.6 | As GCC 5.6 | 3 hard copies and 2no. soft copies |

The Contractor shall keep a copy of the above Contractor’s Documents on Site throughout the term of the Contract.

### 4.6.2.	Design-Build Publications to be kept on Site

The Contractor shall keep the following publications on Site:

- Copy of signed Priced Contract Document

- Copy of a set of Proposal Documents

- Copy of a Price BOQ Document

- Copy of a set of tender drawings

- Copy of a set of Approved Construction Drawings

- Copy of EMP

- Copy of OHS Plan

- Copy of Project Specific Quality Assurance Plan

### 4.6.3.	Progress Reports during the Design-Build

- Progress Reports - Design-Build

The Contractor shall submit Monthly Report progress up to the end of the reporting month within Seven (7) days of the next month or on the next working day (if applicable)

Primavera or similar data-based project portfolio management software shall be used for project management and progress tracking. The project progress schedule shall show the activities planned (Baseline) for the month and percentage progress planned and activities actually executed during the month and their percentage completion. For activities behind the Baseline schedule, provide Delay Analysis and the corrective action needed to recover the situation.

The monthly progress report format shall be as per the template suggested in Annexure A at the end of this section. The report shall contain, but not limited to the following items:

- Project schedule report for critical path analysis and the actions required to recover delay.

- Three (3) Months rolling programme.

- Updated progress S-Curve -To be updated to include an actual curve for overall performance monitoring. If the S-Curve reflect shortages with reference to the baseline curves, recovery measures and action plan are to be submitted to the Engineer in order to recover the lost time.

- Updated resource charts – To be updated to show the actual resources mobilized on site against the baseline figures.

- Diagrammatic layout plans showing physical progress - To identify the extent of work completed in the reporting period and cumulative to date for each major activity or work.

- Digital HD progress photos soft and hard copy (monthly).

- Digital HD video monthly progress soft copy (as required by the Engineer).

Other items required in the Contract or as required by the Engineer from time to time.

1.2	The Contractor shall prepare and submit a Procurement Status Report on a weekly basis for the duration of the Contract. The status report shall include the following:

- List of materials and resources procured; indicate the date/quantity required against the actual date/quantity procured.

- List of materials and resource delivered to the site; indicate the date/quantity required against the actual date/quantity delivered.

- References to all correspondence and transmittals between the Contractor and the Engineer regarding approval of such materials and items.

  - Site Diary shall be generated in Primavera Enterprise and Contract Manager, including but not limited to the following: The diary shall become the property of the Engineer on completion of the Works.

- Visitors to the Site and the reason for the visit.

- Labour on site by trade and its allocation.

- Sub-contractors working on site.

- Material and equipment delivered to site.

- Material and equipment utilized.

- Plant, equipment and tools brought on to or removed from site including hired plant.

- Work progress during the day.

- Verbal instructions requiring written confirmation.

- Temperature and weather conditions.

- Details of any occurrence which may affect the progress of the Works.

- Distribution

All submissions shall be made in Three (3) paper color copies and One (1) set in electronic file format (compact disc), except otherwise specified by the Engineer. The hard copies shall be reproducible from the electronic file copy submitted.

- Schedules - Following joint review, distribute copies of updated schedules to Engineer, Consultant, and Contractor’s project site office, to subcontractors, suppliers, and other concerned parties.

- Reports - Submit copies to the Engineer, Consultant and Contractor’s Site Office.

- Non-Compliance

- If the Contractor fails to submit a Baseline Schedule within Fourteen (14) days after acceptance of Tender, or the Baseline Schedule or Revised Schedule is not Approved by the Engineer within Three (3) months after the first submission, or the Updated Schedule within the time prescribed, then the Engineer shall deduct retention of Ten Percent (10%) of the Contractor’s Progress Payment over and above the 10% Performance Retention Sum until such time that the Contractor has provided submissions that are acceptable to the Engineer.

- The calculation of the Ten Percent (10%) retention to be applied to all subsequent progress payments after the first default and shall be based on the Ten Percent (10%) retention amount due for each progress payment set aside to be accumulated from the time the Engineer considers that the Contractor has failed to make acceptable submissions.

- The sum retained will not earn interest and shall only be released to the Contractor upon due certification by the Engineer that the amount retained may be released to the Contractor.

Annexure A: Proposed Template for Monthly Progress Report Format:

| (MONTHLY REPORT FORMAT) |  |
| --- | --- |
| - OVERVIEW |  |
| - Highlight items of significant achievement and areas of concern in a brief summary for a review of general progress |  |
| - Contract Information Sheet |  |
| - SAFETY |  |
| - Report on the accidents on site |  |
| - Discuss general safety matters including any necessary precautionary |  |
| - CONTRACTOR'S ORGANISATION & RESOURCES |  |
| - Report on staff changes |  |
| - Labour, plant and equipment resources on site |  |
| - PROGRAMME MATTERS |  |
| - Status of programme preparation, submission and updates |  |
| - Highlight changes between actual and programme logic and reasons for the changes |  |

- INTERFACES / KEYDATES

- Completion, handover, interfacing key dates achieved during the reporting period and due in the next six months

- Review and forecast the dates by which the key dates will be achieved

- DESIGN (TEMPORARY WORKS)

- Design development, preparation and submissions

- Design interface and co-ordination with interfacing contractors

- Engineering queries requiring Engineer's urgent attention

- PROCUREMENT / MANUFACTURING / DELIVERY

- Procurement, manufacture, inspection, shipping and delivery status of major plants, equipment and pre-fabricated permanent works

- PROGRESS

- Works in progress and status against accepted Baseline Programme

- Explanations for any progress slippage

- Details of technical difficulties incurred or expected

- Identify areas of delay and details of reasons for delay and of proposals for action to overcome such delays to sustain the progress

- COORDINATION

- Major issues concerning co-ordination with parties in charge of matters affected by the Works or upon which the Works depend

- Discuss actions taken, or action required to resolve matters concerning interface with other parties

- QUALITY MATTERS

- Highlight achievement and shortfall as compared to the Contractor's Quality Plan

- ENVIRONMENTAL AND SOCIAL MATTERS

- Environmental and Social issues, water quality control, noise control, air quality control, odour and complaints

- CONTRACTUAL AND FINANCIAL

- Progress payments

- Contractor's cash flow projection

- Engineer's instructions, variations, quotations

- Claims matters

- AREA OF CONCERN

- MANUALS

- TRAINING

- AS-BUILT DRAWINGS

- ANY OTHER BUSINESS

- ATTACHMENTS

(a) Progress photographs

(b) Engineering status, reports for submitted overdue, held and rejected

(c) List of Contractor's Manpower, Plants & Equipment on site

(d) Material Procurement Status

(e) Sub-contractor list and status

(f) Weather Record Summary

(g) Safety Record and Statistics

(h) List of Site Instructions

(i) List of Variation Orders

(j) List of Quotations

(k) List of Claims

(l) List of Non-Conformance Report (NCR)

(m) Correspondence awaiting Engineer's response and correspondence awaiting Contractor's response

# 5.	Existing Facilities

## 5.1.	Description of the Existing Facilities

The existing Sewer Network comprises of the following

      - Total ten (10 no.) sub catchments to cover Phase-1 area with ten (10 no.) submersible pumping station (SPS).

- Gravity sewer network from each sub catchment area discharges sewage into individual pumping station.

- There are three (3 no.) sea outfalls (Existing – 2No. of 280mm OD HDPE (outfall-1 and2) and 1 No. of 400mm OD HDPE (outfall-3 under construction) which discharges raw sewage to sea.

- The rising main from each of the pumping station is connected to a common sea outfall. The existing system is presented in drawing no. TTI/MUD/MAL/PL/ESN/001B.Rising main from 7 no. SPS is connected to Outfall -1 and rising main from 3 no. SPS is connected to Outfall-2. The Outfall -3 which is under construction will complement the existing two outfalls.

## 5.2.	Contractor’s Responsibilities for Rehabilitation of the Existing Facilities

The contractor shall study the existing pumping system of outfall 1 and 3 (New) and 2 and design/construct/ modify the wet well, pumps, piping, valves, and associated electrical and instrumentation equipment for forwarding the flows to the inlet works of the STP. The contractor shall utilize the existing mechanical/electrical/instrumentation equipment wherever required suitably which has further design life and make all functional to discharge the sewage to the inlet works. Provision to be made to dispose of the sewage to sea in case of emergency.

## 5.3.	Contractor’s Responsibilities for operating the Existing Facilities

## The contractor shall be responsible for operating the diversion scheme which is mentioned in clause 5.2 during the O&M period.

## 5.4.	Employer’s Equipment and free issue materials (Existing Facilities)

No equipment or free materials will be provided by the Employer.

## 5.5.	Incorporation of Existing Facilities into the Works

As per item 5.2 above. The above works will be considered as part of this contract.

# 6.	Demolition, earthworks, construction and commissioning

## 6.1.	General obligations

The Contractor shall:

- provide all of the demolition, excavation, building, co-ordination, repair, review, inspection, testing, quality assurance and control, monitoring, scheduling, clean-up and other construction work and services required for the modification of the Site and the building of the Works.

- undertake all demolition, excavation, and building work in accordance with the Contractor’s Documents specified in these Employer’s Requirements, as approved by the Employer’s Representative where applicable.

- be solely responsible for the construction means, methods, techniques, sequences, and procedures and for coordinating the various parts of the design-build under the Contract.

## 6.2.	Facilities for the Employer’s Personnel during the design build period

The Contractor shall provide suitable transport facility to Employer’s Personnel  (not limited to Car, Van or Bus) during design and build period to attend to the Works executed by the Contractor. The Contractor shall also provide  the required PPE and Safety gear etc to Employer’s personnel and office facility at site when required.

## 6.3.	Contractor’s site access and facilities

Contractor will be given adequate space for labour quarters, material storage. Offsite accommodation for senior staff will have to be arranged by Contractor.

## 6.4.	Electricity, Water and Gas during the Design-Build

Electricity, Water, Telecommunication utilities are available to the site and Contractor shall arrange for necessary connections with the utility agencies and pay for the cost of utilities.

## 6.5.	Employer’s Equipment and free issue items (Design-Build)

Employer will not provide any equipment or other items required by the Contractor and the Contractor shall make his own arrangement to procure those and pay for it.

## 6.6.	Demolition

Not Applicable

## 6.7.	Samples and testing

As per section6.9 and 6.9.6.2

## 6.8.	Payment of Royalties

Payment of royalties, rents and materials etc., shall be borne by the Contractor

## 6.9.	Tests on Completion of the Design-Build

Tests on Completion

6.9.1	General

Prior to the commencement of Tests on Completion the Contractor shall submit for approval the following:

- Site Acceptance Test Documents

- As-Built Drawings

- Operation and Maintenance Manuals

- Site test results / data sheet and photo

Tests on Completion shall not be commenced until the aforementioned documents are approved.

The initial charges of oil, grease, electrolyte, generator fuel / oil, chemical, disposal of cake, etc. necessary for Tests on Completion shall be paid  by the Contractor. Raw sewage and electricity required for Tests on Completion shall be paid by the contractor.

During the initial stages, the sewage receiving the STP may not be as mentioned in earlier sections and in such cases the contractor shall adjust various streams and their units (either shut down certain units for a certain period or by some other means) so that treated sewage qualities are met. If necessary, Contractor shall create design loading conditions for testing purposes by testing fewer than the total number of installed units of process tanks or equipment at a time.

In such cases, multiple tests shall be conducted to ensure that all installed units are tested. The Contractor shall provide adequate notice (this notice period shall be determined by the normal lead time for locally purchased chemicals plus at least 28 days) of his chemical requirements prior to commencement of the Tests on Completion involving their use.

The cost of chemicals used for the Tests on Completion shall be met by the Contractor. The inspection and tests procedure which will be carried out are provided under the general conditions of contract and shall also consist of the following:

- Manual Commissioning Tests (Clause i)

Manual Commissioning Tests shall be such preliminary trials, tests and retests on individual items of Plant or complete systems as are required by the Employer’s Representative in order to demonstrate that the Plant as a whole is ready to undergo the Manual Operation Tests and that these will take place with a minimum of interruption.

The Manual Commissioning Tests shall demonstrate not only the items of Plant under normal operation, but also their response to abnormal and emergency conditions.

The Employer’s Representative will notify to the Contractor which items of Plant will be tested and the extent to which they will be tested in order to fulfill the requirements of the Specification.

Leakage tests at 1.5 maximum working pressures shall be carried out on all erected pipe work prior to the Manual Commissioning Tests.

Pump curves shall be available for the Manual Commissioning Tests and all instruments essential for the tests shall have been calibrated.

- Manual Operation Tests (Clause ii)

When the Manual Commissioning Tests have been completed so that the items of Plant have been demonstrated to the satisfaction of the Employer Representative, the Contractor shall commence the Manual Operation Tests.

These tests shall demonstrate the correct operation of the whole Plant whilst using the minimum quantity of automatic control and monitoring equipment. Such equipment shall be at least that required both for the maintenance of safety and for the normal mode of operation of the Plant.

The Plant will be required to demonstrate satisfactory operation at all design flow rates.

The tests shall be of seven consecutive days' duration; if the supply of water should fail or other matters interfere outside the Contractor's control, the tests may be of such number of broken days as the Employer’s Representative considers is the equivalent.

The exact date of commencement shall be subject to the approval of the Employer’s Representative and shall be dependent on the following conditions having been met

- All relevant items of Plant in approved working order

- All items of Plant correctly identified with labels

- Automatic Commissioning Tests (Clause iii)

The Automatic Commissioning Tests shall be such preliminary trials, tests and retests on individual items of Plant or complete system as are required by the Employer’s Representative in order to demonstrate that the Plant as a whole is ready to undergo the Tests of Completion and that these will take place with a minimum of interruption.

At least one week before the commencement of these tests, the Employer’s Representative will notify the Contractor which items of Plant will be tested and the extent to which they will be tested in order to fulfill the requirements of the specification.

The Tests on Completion as provided under the general conditions of contract shall not be carried out until the completion of the below tests.

- All pipe work shall be hydrostatically tested at site to a pressure equal to 1.5 times the maximum working pressure likely to be encountered in the system.

- The Contractor shall carry out all tests on the Plant and shall supply four copies of all test results to the Employer’s Representative.

- All tests shall be to the approval of the Employer’s Representative who may require them to be repeated, prolonged or modified as may be necessary to ensure that any or all items of Plant conform to the Contract.

- The Employer’s Representative shall be permitted to inspect all Plant which is undergoing tests and may themselves conduct tests.

Where it is necessary for the Employer’s Representative to make arrangements for the supply of water, chemicals, power, etc., for any testing, the Contractor shall not commence the tests until after these arrangements have been made on or after a date agreed by the Employer’s Representative and the Contractor shall make no claim for delay to such testing on this account except as provided under the General Conditions of contract.

If any item of plant fails during or after testing to achieve its intended duty or otherwise proves defective, it shall be modified or altered as necessary and re-tested and re-inspected as required by the Employer’s Representative.

Vibration/noise level tests shall be carried out at site which will form basis for acceptance of the equipment. If the Contractor is not in a position to meet the requirements given below as per ISO 10816 – 1995, the equipment may either be rejected or the Contractor shall carry out all necessary modifications to keep vibrations within the acceptable limits specified.

| Equipment | Noise Level (dBAat 1.00 m from equipment) | Velocity of vibration (mm/sec) |
| --- | --- | --- |
| All rotating equipment not having reciprocating parts with motor kW less than or equal to 15 kW | 85 | 1.12 |
| All rotating equipment not having reciprocating parts with motor kW more than 15 kW and less than or equal to 75 kW | 85 | 1.8 |
| All rotating equipment not having reciprocating parts with motor kW greater than 75 kW | 85 | 2.8 |
| All equipment having reciprocating parts viz. compressors, dosing pumps sampling pumps | 85 | - |

The Contractor shall have a minimum of three commissioning Employer’s Representative, one for process and plant and the other for mechanical/electrical/instrumentation works onsite during all tests in order to both demonstrate the Plant and to correct any faults which may occur.

6.9.2	Dry Test Requirements

As a minimum requirement the following dry tests shall be carried out as a general requirement:

- A general inspection to check for correct assembly and quality of workmanship.

- A check on the presence of lubricant, cooling medium, electrolyte, etc.

- A check on adequacy and security of Plant fixing arrangements.

- A general check to ensure that all covers, access ladders, water proofing, guard railings etc. are in place.

- A check on damp-proofing, rust-proofing and vermin-proofing and particularly the sealing of apertures between building structures, chambers etc. and the outside.

- Civil and Building Works

As a minimum requirement the following dry tests shall be carried out on the civil engineering and building works:

- Check for the presence of foreign bodies in pipe work and structures.

- Mechanical Works

As a minimum requirement the following dry tests shall be carried out on the mechanical systems:

- Carry out preliminary running checks as far is permitted by circumstances in order to ensure smooth operation of Plant.

- Electrical Works

As a minimum requirement the following dry tests shall be carried out on the electrical systems:

- Check phasing and polarity.

- Carry out point to point check on all cables.

- Check on security of cable terminations.

- Check on completeness and adequacy of earthing systems.

- Check setting on protection relays, sizes of fuses and motor overload settings.

- Carry out checks on cabling systems in accordance with the requirements of the relevant standards.

- Check operation of main circuit breakers by secondary injection methods.

- Check rotational direction of Plant.

- Check instrument loop integrity, functionality and calibration.

- Check operation of standby generator installation and mains / generator changeover procedures; a 4-hour load test (using the normal load of the Works) shall be carried out on the generator when the load is available.

- Check plant functionality.

- Check functionality of the central MMI and its power supply.

- Process Plant Item / Equipment

All process plant items / equipment shall be tested to ensure they meet the Employer’s Requirements for quality of workmanship, construction and performance.

- Hydraulic Wet Test Requirements

Hydraulic wet tests shall be carried out on completion of dry tests.

Clear Water shall be used for hydraulic wet tests. The purpose of the tests is to prove the hydraulic performance of the Works. In order to demonstrate this, the Contractor shall ensure that each part of the Works is hydraulically loaded to its rated throughput for a period of at least four hours.

In order to ensure a sufficient supply of water to carry out these tests the Contractor shall provide all required facilities, including but not limited to any temporary facilities that may be required for storage and recycle of Clear Water or facilities for the disposal of the water off Site in an approved manner.

The following tests inter alia shall be carried out:

- Pressure testing of all piped systems laid direct in ground in accordance with the relevant standards.

- Fill all structures and check for leaks.

- Filling of all storage vessels to check for leaks and distortion.

- Running of all pumped systems in order to check for.

- Correct functionality.

- Absence of leaks.

- Correct running temperatures.

- Smoothness of running and the absence of undue vibration or stress.

- Check drive running currents.

- Carry out calibration of instruments where appropriate

- Carry out valve operation, diversions etc. to fully hydraulically load each process element (or where there is a requirement to withstand an over load), overload each process element.

- Demonstrate correct functionality of electrical, control and instrumentation systems.

- The Contractor shall simulate the conditions that will prevail when operating as a process in order to demonstrate the correct functionality of process control loops etc.

- During these tests a check on the performance of Plant shall be made to compare its site performance with the factory test data and to identify any constraints on performance due to site conditions.

6.9.3	Safety Audit

After satisfactory completion of hydraulic wet tests and prior to introduction of process fluid to the plant a safety audit shall be carried out to ensure compliance with the necessary requirement for safety and for operation of Plant. The safety audit shall be documented. The safety audit document shall be approved by the Employer’s Representative prior to commencement of Plant commissioning.

6.9.4	Process Wet Tests (with Raw Sewage)

On approval by the Employer’s Representative the Contractor shall carry out process wet tests. Raw Sewage shall be used as the main feed stock for process wet tests. These tests shall be carried out to demonstrate the process performance of the Works. In order to demonstrate this, the Contractor shall ensure that each part of the Works is loaded to its rated throughput (including a period of overload if required in order to demonstrate compliance with the Employer’s Requirements) for a continuous stable operating period of not less than 48 hours. If necessary, Contractor shall create design loading conditions for testing purposes by testing fewer than the total number of installed units of process tanks or equipment at a time. In such cases, multiple tests shall be conducted to ensure that all installed units are tested.

Whenever raw sewage is used for testing, the Contractor shall keep a bowser on standby to remove the wastewater for safe disposal in the event  anything goes wrong with  the wet tests.

The Contractor shall provide all required facilities for the disposal off Site in an approved manner.

The following tests inter alia shall be carried out:

- Check for leaks on vessels, structures, pumps and pipe work.

- Running of all pumped systems in order to check for.

- Correct functionality.

- Absence of leaks.

- Correct running temperatures.

- Smoothness of running and the absence of undue vibration or stress.

- Check drive running currents where the solution pumped is different from that pumped during hydraulic wet tests.

- Carry out calibration of instruments.

- Carry out valve operation, diversions etc. to fully hydraulically load each process element (or where there is a requirement to withstand an over load), overload each process element.

- Demonstrate correct functionality of electrical, control and instrumentation systems not checked during dry or hydraulic wet tests or which may have changed as a result of the different operating conditions now prevailing.

On completion of the tests on the various parts of the works the Contractor shall run the plant as a whole in order to demonstrate the full functionality and performance of the Works at various throughput rates for a continuous period of not less than 7 days.

During the various process tests the Contractor shall perform sampling and analysis of all the process streams (locations) and parameters listed in the “Sampling/Analysis Locations and Frequencies” table provided in the “Tests after Completion” Section below. The frequencies listed in this table shall be followed for the Tests after Completion. However, for the Process Wet Tests performed as part of the Tests on Completion, the sampling frequency for all locations and all parameters shall not be less than once every hour. The Contractor shall demonstrate to the Employer’s Representative that the Works is functioning in accordance with the Employer’s Requirements. Each sample shall comprise two 1 litre (minimum) quantities and shall be labeled to identify the contents, where taken and time and date. The flow recorded at the time of sampling shall also be indicated in the log book or record. One sample shall be used by the Contractor for his analysis; the other shall be handed over to the Employer’s Representative.

The Employer’s Representative reserves the right to take additional samples and to carry out his own tests or to check the samples taken by the Contractor.

The Employer’s Representative shall be given reasonable access to the premises where analysis is taking place in order to check on working practices and the procedures being adopted.

6.9.5	Effluent Quality Criteria for Passing the Tests on Completion

The Works shall be considered to have achieved the required effluent quality standards for passing Tests on Completion if all samples taken during a 15-day continuous operational period comply with the criteria set down for passing the Tests after Completion. This includes criteria relating to the reliability of the plant.

The Effluent Quality Tests on Completion shall not be commenced until all tests associated with the civil/building, electrical and mechanical works and individual process tests have been completed to the satisfaction of the Employer’s Representative.

6.9.6	Tests after Completion

6.9.6.1	General

On successful completion of “Test on Completion” the Contractor shall carry out over a period of time not exceeding two months two separate 30 days operational tests. These tests shall be used to prove the operation of the Works at varying flows and with varying raw Sewage quality. During these tests Effluent produced by the Works will be entering the disposal system.

The timing of the tests shall be determined by the Employer who shall give notice to the Contractor in accordance with the General Conditions of Contract. The total time for carrying out the tests shall not be less than two calendar months. One of the tests for each part shall be carried out in a period of high raw Sewage BOD and suspended solids.

On commencement of each 30-Days test the Employer shall allocate a continuous period of not greater than 60 days to complete the test. Any failure to perform during the 60days period shall restart the “30-day clock”. If the part of the Works fails to pass the test in the 60 days period the test shall be deemed as a failure and the Contractor shall carry out any necessary remedial work to the satisfaction of the Employer’s Representative before the Contractor restarts the test.

During the tests the Contractor shall take samples to demonstrate that the part of the Works is performing in accordance with the Employer’s Requirements. The procedure for taking the samples shall follow the pattern adopted for Test on Completion. Samples shall be taken at locations and intervals detailed below. The results of the Tests after Completion shall be compared and evaluated by the Employer and Contractor.

The Contractor will not be held responsible for interruptions to the sewage treatment process as a result of Grid power failures (unless as a result of a Plant failure) interruptions in the raw Sewage supply etc. which are out of his control. However, the Contractor shall be required to demonstrate that the Works can cope with these inevitable interruptions in an orderly fashion and recover to a normal operational state with the minimum of manual intervention.

All consumables except power needed for operation of the Works and transportation of sludge off site shall be provided by the Contractor.

The Contractor shall provide all facilities and equipment not supplied under the contract and which are deemed necessary for the Contractor to carry out and monitor the Tests after Completion.

6.9.6.2	Sampling and Analysis (for Test on Completion and Test after Completion)

Sampling and analysis shall be performed to measure the parameters indicated in the table under clause 3.10.2, at the locations and frequencies indicated in the table. In case of multiple units (such as multiple aeration basins or thickeners), the indicated sampling and analyses shall be performed for each individual module.

The Contractor shall employ an Approved Laboratory to take composite samples from the Works each day during the Test after completion performance test period, as follows:

• One 24-hour composite flow-weighted sample of the influent sewage

• One 24-hour composite flow-weighted sample of the secondary effluent

• Composite flow-weighted sample of the final effluent

All costs associated with the taking and analysis of samples shall be met by the Contractor. The  analysis shall be carried out by chemical certified laboratory (Government Certified) and as approved by the Employer’s Representative, and shall be performed in strict compliance with appropriate analytical methods published in British Standards, or in “Standard Methods for the Examination of Water and Wastewater” published by the American Public Health Association, or as published by the US Environmental Protection Agency. The Contractor shall submit to the Employer’s Representative a comprehensive report of the above sampling and analysis, including details of each analytical test as well as a summary of all the data and results in a Microsoft Excel spreadsheet.

6.9.7	Criteria for Passing the Test after Completion

- Treated Effluent and Dewatered Sludge Quality Criteria

The Works shall be deemed to have met the Treated Effluent and Dewatered Sludge Quality Criteria if:

- at least 95 percent of the plant effluent samples described above meet the requirements specified under the “Effluent Quality Requirements” and at least 95 percent of the dewatered sludge samples described above meet the requirements specified under the “Dewatered Sludge Quality Requirements”

- Operational Cost Criteria

The plants shall have fulfilled the operating cost criteria if the operating costs determined during the Tests After Completion are in agreement with or less than those detailed in the Contractor’s Functional Guarantee or an amount of liquidated damages are agreed by the Contractor and the Employer’s Representative to compensate for any short fall in performance up to an agreed maximum amount if stated.

- Plant Reliability Criteria

A part of the Works shall be deemed to have failed its test if:

- A single item of Plant / equipment fails more than twice during the test.

- More than four individual Plant items / equipment fail.

An item of Plant / equipment shall be deemed to have failed if manual intervention is required in order to restore the Plant / equipment to its fully operational state: i.e. the failure of a duty drive will be considered as one failure, if the standby drive fails to start that will be considered as a second failure.

6.9.8	Performance Certificate

The conditions for issuance of a Performance Certificate as detailed in the Conditions of Contract shall inter alia comprise:

- The completion of the two months operation of the Works (Tests after Completion) to the satisfaction of the Employer’s Representative.

- The O & M Manuals have been updated following one year’s operational experience and approved by the Employer’s Representative.

- All defects identified prior to Taking Over and defects identified during one-year operation of the Works have been rectified.

- All Tests “After Completion” have been completed to the satisfaction of the Employer’s Representative.

- All training detailed in the Employer’s Requirements has been completed.

# 7.	Operation Management Requirements

## 7.1.	General Requirements

### 7.1.1.	Overall description of the Operation Service

The Contractor shall,

- operate and maintain the Works;

- receive wastewater influent from the sewer;

- treat wastewater to meet the specified standards and safely discharge the treated wastewater into the environment (or at the specified discharge point);

- treat and store sludge and other screenings and grit materials and transport such wastes from the Site for safe disposal, as further specified in these Employer’s Requirements;

- carry out monitoring, sampling, testing and reporting in accordance with the approved Wastewater Quality Testing Plan;

- undertake all preventive and routine maintenance, including repainting of buildings and other structures in accordance with the Contractor’s maintenance management program;

- plan and carry out all necessary asset replacement whether funded through the Asset Replacement Fund or otherwise;

- procure at its own expense all things necessary to operate and maintain the Works including labour, plant, equipment, electricity, stand-by power, chemicals, materials, and spare parts;

- fence and secure the Works and prevent unauthorized access;

- maintain the site in tidy condition and take measures to control potential environmental nuisance, including but not limited to, odours, litter, pests, insects, rodents and birds;

- develop and manage programs to train and advance the skills of the Contractor’s Personnel;

- provide familiarity training to nominated staff of the Employer and Employer’s Representative;

- carry out all management, financial and administrative responsibilities relating to the Works,

- manage complaints from the public;

- provide periodic reports on the operation and performance of the Works.

### 7.1.2.	Performance during the Operation Service Period

- The Contractor shall ensure that the Works complies at all times with:

- The conditions of any license or consent issued by the regulatory authorities; and

- The minimum standards specified in the Schedule of Performance Standards; and

- Any additional requirements set out in these Employer’s Requirements.

- The Contractor shall at all times operate and maintain the Works in accordance with the approved Environmental Management Plan and approved Contractor’s Documents including:

- the Operating and Maintenance Manuals

- the Emergency Response Plan

- the Wastewater Quality Testing Plan

- the Health and Safety Manual

- the Quality Assurance Manual

- Where no specific performance standard exists in the Contract the Contractor shall at all times operate and maintain the Works in accordance with good international wastewater utility practice;

- Except as may be authorized by the Employer’s Representative during periods of planned maintenance, the Contractor shall ensure that the minimum dry weather and peak flow design capacity is made available at all times during Operation Service Period.

### 7.1.3.	Employer’s Equipment and free issue materials (Operation Service)

### During the Operation Service, the Contractor shall procure everything else required such as raw materials, fuels, electricity, consumables and etc., and pay for their cost. The Employer may assist the Contractor to get permits etc., if required.

## 7.2.	Contractor’s Documents (Operation Service)

### 7.2.1.	General Requirements for Contractors Documents (Operation Service)

With respect to each of the Contractor’s Documents listed in this section the Contractor shall meet the following requirements:

- The Contractor shall submit each of the Contractor’s Documents to the Employer’s Representative for its review only, review and consent or review and approval in accordance with the schedule in Section 7.2.2 below and GCC Sub-Clause 5.2;

- The Contractor shall begin the implementation of the Contractor’s Documents upon receiving consent or approval from the Employer’s Representative;

- The Contractor’s Documents shall be implemented by the Contractor at the Contractor’s expense;

- The Contractor shall review and update the Contractor’s Documents in accordance with the schedule in Section 7.2.2 below. However, routine updates to the Operating and Maintenance Manuals shall not be subject to approval by the Employer’s Representative. Updates to other plans and manuals shall require approval or consent as indicated in GCC 7.2.2.

- A physical copy of all plans and manuals shall be retained at the Site at all times and available for inspection by the Employer’s Representative.

### 7.2.2.	Submission and approval of Contractor’s Documents (Operation Service)

The Operation Service plans and manuals shall be submitted in accordance with the following timetable:

| Item | Initial submission date | Update frequency | ER review only, review and approval, or review and consent required?1 | Number of copies to be supplied (see GC 1.9) |
| --- | --- | --- | --- | --- |
| Operating and Maintenance Manuals | 6 months prior to operations | Continuously following modification of assets and/or procedures | Review and approval (as GCC 9.12). Updates do not require approval. | 3 hard copies and 2no. soft copies |
| Emergency Response Plan | 6 months prior to operations | Annually | Review and approval | 3 hard copies and 2no. soft copies |
| Wastewater Quality Testing Plan | 6 months prior to operations | Semi- Annually | Review and approval | 3 hard copies and 2no. soft copies |
| Health and Safety Manual (Operation Service) | 6 months prior to operations | Annual | Review and approval | 3 hard copies and 2no. soft copies |
| Quality Assurance Manual | 6 months prior to operations | Annual | Review and approval | 3 hard copies and 2no. soft copies |
| Add additional documents as needed. |  |  |  |  |

The Contractor shall keep a copy of the above Contractor’s Documents on Site throughout the term of the Contract.

7.2.3.	Operation Service Publications to be kept on Site

The Contractor shall keep the following publications on Site:

All drawings, equipment manuals and records of maintenance.

### 7.2.4.	Operating and Maintenance Manuals

Operation and Maintenance Manuals shall include sufficient detail to operate, maintain, dismantle, reassemble, adjust and repair the Plant and Works and shall include, as appropriate:

- a description and schematic of the Works showing the individual process stages forming the Works. The schematic shall indicate the sequence of the treatment units and show all chemical feed points;

- facility design criteria and capacities, including the dimensions and rated capacity of all equipment;

- step-by-step operating instructions for all major components and unit processes used at the plant. The section shall also cover all the operating conditions routinely or periodically encountered, including start-up procedures, shut down procedures, and emergency operating procedures;

- chemical management procedures, including step-by-step instructions to be used to store, handle, and feed each chemical used at the facility;

- Maintenance procedures, including, preventative maintenance schedules, calibration schedules, lubrication schedule, step-by-step maintenance instructions whenever possible, parts inventory and manufacturer/parts supplier/vendor details;

- Instrument calibration procedures and schedules;

- Record keeping requirements (daily logs, maintenance records, routine reports, engineering drawings, equipment specifications, warrantees, instruction manuals, training records, etc.).

### 7.2.5.	Emergency Response Plan

The Contractor shall prepare an emergency response plan (the “Emergency Response Plan”) to manage emergencies covering,

- major plant failures;

- chemical spills;

- illegal discharges into the upstream sewer network;

- pollution of the environment;

- extreme weather conditions;

- natural disasters;

- accidents

- other similar emergencies

The Contractor shall include in the Emergency Response Plan:

- contingency plans for all identified emergencies;

- the identities of key Contractor and Employer emergency response coordination staff, together with emergency contact details;

- procedures to provide immediate notification to the Employer’s Representative upon the occurrence of any emergency;

- the location of emergency equipment and other resources;

- training programs for the Contractor’s staff; and

- an annual program for emergency response exercises.

### 7.2.6.	Wastewater Quality Testing Plan

The Contractor shall develop a wastewater quality testing plan (the “Wastewater Quality Testing Plan”). The Wastewater Quality Testing Plan shall include:

- details of the laboratory and testing equipment and instruments used at the plant;

- location of monitoring and sampling points;

- methods, procedures, schedules and frequencies of sampling and analysis of wastewater influent and effluent quality, including procedures for validation of test results if an initial test indicates that a specified standard has been breached;

- methods, procedures, schedules and frequencies of sampling and analysis of sludge and other screening materials;

- step-by-step instructions for each laboratory test the plant conducts;

- a plan to monitor smell, noise and other local environmental impacts;

- a program to monitor whether the Works is complying with Environmental Management Plan;

- a detailed protocol for immediately notifying the Employer and any relevant regulatory authority of any failure to meet the specified standards;

- a protocol for addressing any non-compliance of the Works

- methods for testing the accuracy of instruments; and

- calibration schedules, with frequencies and methods for calibration of the different instruments.

- procedures for audit and validation of test results;

- protocols for documentation of sampling and analysis results;

The methods and frequencies of sampling and testing in the Wastewater Quality Testing Plan shall comply with the requirements of the regulatory authorities, and with the methods and frequencies specified in these Employer’s Requirements.

### 7.2.7.	Health and Safety Manual (Operation Service)

The Contractor shall develop written health and safety procedures (the “Health and Safety Manual”) covering all aspects of the operation and maintenance of the Works, including (but limited to):

- Health and safety hazard analysis;

- Health and safety precautions;

- Personal protective clothing and equipment and safety gear;

- Procedures for dealing with a health and safety incident;

- Health and safety staff responsibilities;

- Use of, storage of, safety arrangements, and evacuation procedures in connection with chemical facilities;

- Confined space entry procedures;

- Safety measures to manage risks from the build-up of methane and other noxious gases;

- Fire equipment inspection procedures.

### 7.2.8.	Quality Assurance Manual

The Contractor shall develop a quality assurance manual (the “Quality Assurance Manual”) in accordance with the requirements of GCC 4.9 and EN ISO 9001. The quality assurance system shall be ISO approved and certified.

## 7.3.	Staff organisation and training

### 7.3.1.	Staff organization

No later than 21 days before the date of commencement of the Operation Service the Contractor shall submit to the Employer’s Representative, for approval, a staffing plan showing:

- the Contractor’s proposed organization for carrying out the Operation Service.

- the names, qualifications and experience of all operation and maintenance personnel.

The Contractor shall promptly inform the Employer’s Representative in writing of any changes to its staffing or organizational arrangements.

The Contractor shall ensure that its staff has expertise and experience consistent with the requirements specified in Section 8 of these ER.

### 7.3.2.	Training of Contractor’s Personnel

The Contractor shall prepare and implement a staff training plan (the “Staff Training Plan”) for the training of the Contractor’s operations and maintenance staff. The Staff Training Plan shall be submitted to the Employer’s Representative for comment but shall not require the approval of the Employer’s Representative.

The quality and effectiveness of the Contractor’s training programmes shall form part of the audit of the Contractor’s performance undertaken by the Auditing Body under GCC 10.3.

### 7.3.3.	Training of Employer’s Personnel

The Contractor shall provide familiarity training on an as-needed basis to nominated members of the Employer’s and Employer’s Representative’s supervisory staff covering the design, operation and maintenance of the Works and the Contractor’s procedures for reporting and quality control.

## 7.4.	Health and safety

The Contractor shall:

- Ensure that its operating and maintenance procedures follow good health and safety practice;

- Ensure that the Works is maintained at all times in a safe condition.

- Train all its staff on health and safety issues in accordance with the Health and Safety Manual and the Staff Training Plan;

- Provide for all staff and visitors the necessary protective and safety equipment and clothing.

- Provide all necessary safety and first aid equipment.

The Contractor’s staff shall include an Accident Prevention Officer who shall be responsible for safety at the Works. The Accident Prevention Officer shall be properly qualified and experienced in wastewater treatment safety matters. The Contractor shall notify the Employer of the identity of the Accident Prevention Officer.

The responsibilities of the Accident Prevention Officer shall include:

- safety training

- safety inspections, and

- promoting good safety practice

- investigation of accidents and health and safety breaches.

- the inspection and maintenance of fixed and portable fire protection equipment

## 7.5.	Treatment and disposal of wastes from treatment operations (if applicable)

All wastes from the treatment operations shall be disposed of at the approved disposal area at Hulhumale’ waste disposal site at Contractor’s cost.

- Requirements for storage of sludge on site and transport of sludge for disposal ( refer to  3.11.14;

- Acceptable and non-acceptable ( dumping in the sea) methods of sludge disposal;

- The location of approved disposal sites (Waste transfer center, Hulhumale’.);

- The Contractor’s obligations to obtain approval from the Employer’s Representative for any changes to the disposal site or method;

- The Contractor’s responsibilities for payment of amounts due for the disposal of wastes;

- Ownership of any revenues from the beneficial sale of sludge.

## 7.6.	Maintenance requirements

### 7.6.1.	General maintenance provisions

The Contractor shall carry out maintenance of all Plant and equipment in accordance with the manufacturers’ recommendations and the Operation and Maintenance manuals. The specification of spare parts, in terms of the materials used and the quality of manufacture shall be in accordance with the recommendations of the original manufacturer.

The Contractor shall ensure that buildings and ancillary structures are kept clean and continuously maintained in a proper and orderly fashion. The Contractor shall maintain, repair, paint, and replace all structures, building elements (including fittings and services), and office furniture as necessary to maintain the appearance and functionality of the Works.

The Contractor shall maintain outside spaces in a tidy condition and undertake maintenance of paved areas, lawn areas, plants, shrubs, bushes and trees.

### 7.6.2.	Maintenance management system and inventory control

The Contractor shall develop and implement a computerized maintenance and inventory control system which shall include, but not be limited to:

- a system for planning and scheduling preventative maintenance works;

- a system for spare part inventory control;

- a system for recording all preventative and reactive maintenance carried out by the Contractor.

## 7.7.	Measurement and testing during the Operation Service Period

### 7.7.1.	General

The Contractor shall undertake all monitoring, sampling and testing in accordance with:

- The minimum frequencies and sampling methods specified in these Employer’s Requirements;

- The approved Wastewater Quality Testing Plan;

- The Environmental Management Plan;

- Any additional requirements specified by the applicable regulatory authorities.

### 7.7.2.	Flow measurement

The Contractor shall monitor and report on:

- The volume and rates of flow of wastewater received at the Works

- The volume and rates of flow of treated wastewater discharged from the Works

- The volume and rates of flow of untreated wastewater discharged via overflows or other bypass arrangements.

Meters and flow measurement devices shall be checked and recalibrated every two years, or in accordance with the manufacturer’s recommendations if more frequent testing is recommended.

### 7.7.3.	Sampling methods and frequencies

The sampling and minimum testing frequency during the O&M period shall be as per clause 3.10.2

| Parameter | Type of sampling (Composite) | Frequency of testing |
| --- | --- | --- |
| BOD5 | 24-hour flow proportional samples | Daily |
| Chemical Oxygen Demand | 24-hour flow proportional samples | Weekly |
| Total suspended solids | 24-hour flow proportional samples | Daily |
| As per clause 3.10.2 |  |  |

### 7.7.4.	Measurement of smell and noise

Odour sampling shall be carried out by the Contractor at random intervals as per the maintenance plan submitted by the contractor on a Daily/Weekly/Monthly basis. Noise monitoring shall be carried out by the Contractor on a random basis as mentioned above.

### 7.7.5.	Third party validation of results

In order to check and validate the Contractor’s laboratory results, the Employer’s Representative may at any time:

- authorised third parties to take samples and undertake independent testing on its behalf; and

- require the Contractor to take samples on its behalf and to have such samples tested at an independent laboratory.

## 7.8.	Asset Replacement

When an asset is to be replaced pursuant to GCC Sub Clause 14.5 (Asset Replacement Schedule) and GCC 14.18 (Asset Replacement Fund) the specification of the replacement asset shall be on the basis of “equal or better” and the design life of the replacement asset shall be in accordance with the asset life table in Section 4.5 of these Employer’s Requirements.

## 7.9.	Reporting requirements during the Operation Service Period

### 7.9.1.	Information to be notified immediately

The Contractor shall immediately notify the Employer’s Representative in the event of the following:

- A variation in the characteristics of wastewater influent which is indicative of an illegal discharge into an upstream sewer;

- A major breakdown of the Works;

- A major accident or pollution incident;

- A failure to meet the treated effluent discharge standards specified in the Schedule of Performance Standards.

### 7.9.2.	Monthly progress report

Within 7 days of the end of each calendar Month, the Contractor shall submit a monthly report to the Employer’s Representative summarizing the technical performance, staffing and operation and maintenance of the Works. The layout of the reports and other general requirements shall be discussed and agreed with the Employer’s Representative.

The Monthly report shall include:

- monthly influent flow rate graphs and tables showing daily maximum, average and minimum inflow values;

- laboratory average daily, weekly and monthly results tabulated with maximum and minimum values;

- quantities and quality of sludge and other waste materials and records of delivery to disposal site;

- a report on Plant and Works outages;

- a summary of compliance with the Performance Standards;

- records of consumption of electricity and chemicals;

- a summary of Plant and equipment repair, overhaul, and replacement activities undertaken in the Month;

- asset replacements carried out under the Asset Replacement Fund;

- a report on exceptional events, emergency operations, and accident statistics during the Month;

- a summary of complaints received from the public;

- a programme for major Plant maintenance and asset replacement for the following three Months;

- any other data reasonably requested by the Employer’s Representative

The Monthly report shall be submitted in electronic form only.

### 7.9.3.	Annual report

The Contractor shall, each year, prepare and submit an Annual report summarizing the Contractor’s performance of the Operation Service in the previous year. The format and scope of the Annual report shall be discussed and agreed in advance with the Employer’s Representative. The reports shall summaries the data provided in the Monthly reports.

The timing of annual reports (for instance, whether they should be aligned to Calendar years or Contract year) shall be as specified by the Employer’s Representative. The Annual report shall be submitted no later than 28 days following the end of the reporting year.

### 7.9.4.	Documents to be held on site during the Operation Service Period

The Contractor shall at all times hold the following documentation on Site during the Operation Service Period:

- Contractor’s Documents (Design-Build) listed in Section 4.6

- Contractor’s Documents (Operation Service) listed in Section 7.2

- Environmental Management Plan

- Commissioning testing records and Commissioning Certificate

- SCADA records, sampling and testing records, calibration records, incidence and failure records, and safety records.

# 8.	Contractor’s Staff and expertise

## 8.1.	General

The Contractor’s Personnel shall have qualifications and experience consistent with the requirements specified in Table 8.1 and 8.2.

The Contractor is encouraged to use local labour that has the necessary skills and is required involve MWSC in the recruitment process. The following table represents a sample qualification and pay structure of MWSC and it is important to align this with the contractors’ staff and expertise as the staff are planned to be later absorbed in to MWSC.

| Detail | Education | Experience in relevant field | Additional / Special Skills Requirement | Salary Range (with variable allowances) |
| --- | --- | --- | --- | --- |
| Manager / Lead Engineer (STP Manager) | Master's Degree (MBA or Relevant Engineering Field (With) Bachelor’s Degree in relevant Engineering Field | -04 years' experience in a related field. - Minimum 02 years' experience in managerial lead / principal engineer role. | -Leadership & Management Skills -Financial Management -People Management Skills -Strategic Management skills -Analytics Skill -Able to work autonomously | MVR 30,000.00 – MVR 27,000.00 |
|  | Bachelor’s Degree in relevant Engineering Field | -07 years' experience in a related field. -Minimum 02 years' experience in managerial lead / principal engineer role. |  |  |
| Assistant Manager / Senior Engineer (Assistant STP Manager) | Master's Degree (MBA or Relevant Engineering Field (With) Bachelor’s Degree in relevant Engineering Field | -03 years' experience in a related field. -Minimum 02 years' experience in managerial senior engineer role. |  | MVR 25,000.00 – MVR 22,000.00 |
|  | Bachelor’s Degree in relevant Engineering Field | -05 years' experience in a related field. -Minimum 02 years' experience in managerial senior engineer role. |  |  |
| Senior Officer / Engineer (Process Control Engineer) | Bachelor’s Degree in relevant Engineering Field | -Minimum 03 years' experience in a supervisory engineer level | -Leadership Skills -People Management Skills -Analytics Skill -Able to work autonomously | MVR 18,000.00 – MVR 21,000.00 |
| Assistant Engineer (Assistant Process Control Engineer) | Bachelor's Degree / Graduate Certificate | -No Experience Required. |  | MVR 14,000.00 – MVR 17,000.00 (excluding OT) |

All supervisory personnel employed at the Site shall be able to read, write and converse in the ruling language of the Contract specified in PCC 1.4.

Table 8.1 Qualifications and Experience – Design Build

| Position | Qualifications required | Experience required |
| --- | --- | --- |
| Design Manager | Degree in Chemical, Civil or Mechanical Engineering from an internationally recognized University | Minimum of 25 years relevant experience including Design, operation of large sewage treatment plants and nutrient removal plants, direct labour supervision experience gained in overseas environment dealing with an expatriate labour force of various nationalities, sound practical background, computer literate for the engineering field. Fluent in English both written and spoken with an excellent capability in written technical skills as well as oral and written communication skills. Computer literate. |
| Process designer | Degree in Chemical / Civil Engineering (respectively) from an internationally recognized University. | Minimum of 15 years relevant experience including direct labour supervision experience gained in overseas environment dealing with an expatriate labour force of various nationalities. |
| Construction Manager | Degree in Civil Mechanical Engineering (respectively) from an internationally recognized University | Minimum of 10 years relevant experience in construction of large sewage treatment plants and nutrient removal plants, direct labour supervision experience gained in overseas environment dealing with an expatriate labour force of various nationalities, sound practical background, computer literate for the engineering field. Fluent in English both written and spoken with an excellent capability in written technical skills as well as oral and written communication skills. Computer literate. |
| Safety, Health and Environment Officer | ##### Corporate Member of the Institute of Occupational Safety and Health (IOSH) and a Registered Safety Practitioner or equivalent qualification from an internationally recognized body. | At least 5 years’ experience of Occupational Safety Management in an industrial environment. Good command of the English language both written and spoken. Good communicator. |
| Quality Assurance Manager | University degree in relevant field or equivalent qualification from an internationally recognised body. | At least 5 years’ experience of Quality Assurance and Quality Control in an industrial environment. Leadership skills. Good command of the English language both written and spoken. Good communicator. |

Table 8.2: Qualifications and Experience – Operation Service

| Position | Qualifications required | Experience required |
| --- | --- | --- |
| STP Manager | Degree in Chemical, Civil or Mechanical Engineering from an internationally recognized University as approved by the Republic of Maldives. | Minimum of 10 years relevant experience including operation of large sewage treatment plants and nutrient removal plants, direct labour supervision experience gained in overseas environment dealing with an expatriate labour force of various nationalities, sound practical background, computer literate for the engineering field. |
| Safety, Health and Environment Officer | Corporate Member of the Institute of Occupational Safety and Health (IOSH) and a Registered Safety Practitioner or equivalent qualification from an internationally recognised body. | At least 5 years experience of Occupational Safety Management in a similar industrial environment. |
| Process control engineer | Degree in Electronics or Instrumentation Engineering from an internationally recognized University. | At least 5 years experience in a similar industrial environment including operation of large capacity waste water treatment plants. |
| etc. |  |  |

# 9.	Hand-Back Requirements

## 9.1.	General requirements

At the Contract Completion Date, the Works shall be:

- in a reasonable condition of repair, cleanliness and appearance taking into account its age and allowing for reasonable wear and tear; and

- capable of meeting the standards specified in the Schedule of Performance Standards.

The procedures for testing, inspection and remedying of defects prior to hand back shall be as detailed in the GCC 10.8.

## 9.2.	Hand-back inventories

At the Contract Completion Date the Contractor shall hand-over the following stocks of consumables, spare parts and special tools:

- Spare parts sufficient for [6] Months operation of the Works based on manufacturer’s recommendations;

- Chemicals sufficient for [1] Months operations;

- Fuel stock for the emergency generators sufficient for [2] weeks of continuous operation;

- Other consumable supplies (e.g. lubricants etc.) sufficient for [insert number] Months of the operations;

- All special tools as are necessary to carry out maintenance in accordance with the manufacturer’s recommendations.

- The Contractor shall provide a complete Plant inventory and data sheets for each item of Plant installed within the Works.It should also include supplier and servicing agent details.

- Two copies of all programmes relating to all programmable devices, PLC Graphics Systems, SCADA Systems comprising System CDs/Diskettes and System Documentation shall be supplied by the Contractor prior to issue of the Performance Certificate. A licensed copy of the programming software shall be provided.

No less than six months prior to the Contract Completion Date, the Employer and the Contractor shall meet and agree on a detailed inventory of spare parts, special tools, and consumables to satisfy the requirements indicated above.

For the avoidance of doubt, the above inventories shall be provided at the Contractor’s expense.

## 9.3.	Training of Employer’s follow-on O&M personnel

No less than eight months prior to the Contract Completion Date, the Contractor shall prepare and deliver to the Employer for its approval a training plan for the Employer’s follow-on O&M personnel (or personnel designated by the Employer). The aim of the training plan shall be to equip the follow-on O&M personnel with the knowledge and skills necessary to operate and maintain the Works.

Following approval of the training plan the Contractor shall provide formal and on-the-job training for up to 10 personnel in accordance with GCC 10.5.

The training shall cover at least the following:

- managing, operating, controlling, monitoring and maintaining the Works, the individual treatment processes and all associated plant and equipment;

- data filing and processing and reporting;

- assembly, dismantling and maintenance of equipment and plant;

- fault diagnosis and rectification

- the Operation and Maintenance Manuals,

- the Health and Safety Manual

- the Emergency Response Plan

- the Wastewater Quality Testing Plan

- Quality Assurance Plan

All training shall be completed by the end of the Operation Service Period.

The Contractor shall bear the cost of planning the training program and providing trainers, training materials and training venues. The Employer shall be responsible for all wages, travel and subsistence associated with the participation its nominated personnel in the approved training program.

# 10.	Terms of appointment for the Auditing Body

## 10.1.	General

The Contractor shall engage and pay for the Auditing Body specified in GCC Clause 10.3 using the provisional sum amount included in the Contract Price for the Operating Service.

The terms of the agreement between the Auditing Body and the Contractor shall be subject to the approval of the Employer.

## 10.2.	The procedure for appointment of the Auditing Body

Procedure for the appointment of the Auditing Body shall be as follows:

- The Contractor shall propose a shortlist of a minimum of 3 candidates for the approval of the Employer.

- If the Employer requires the removal of a candidate from the shortlist in (a) above, then the Contractor shall remove such candidate and shall propose a substitute candidate for the approval by the Employer.

- Following approval of the Contractor’s shortlist, the Contractor shall undertake a competitive procurement of the Auditing Body from the agreed shortlist.

- The procedures for procurement, evaluation and selection, and the terms of appointment, of the Auditing Body shall all be subject to the approval of the Employer.

If the Parties cannot agree on the appointment of the Auditing Body the matter shall be referred to the DAB for resolution.

The appointment of the Auditing Body shall be for a period of three years unless otherwise agreed by the Parties.

## 10.3.	Reappointment procedure

The Auditing Body’s appointment may be renewed subject to the agreement of both parties. If either party objects to the renewal of the Auditing Body, then the Parties shall appoint an alternative Auditing Body following the same procedure as above.

## 10.4.	Scope of services of the Auditing Body

The Auditing Body shall audit and monitor the performance of the Contractor, the Employer and Employer’s Representative. Notwithstanding that the Auditing Body is engaged by the Contractor; the Auditing Body shall act independently and impartially.

The scope of services of the Auditing Body shall include the following:

- To assess the overall performance of the Contractor;

- To review the quality and comprehensiveness of the plans and manuals submitted by the Contractor;

- To review the Contractor’s procedures for testing, reporting and quality control;

- To undertake sample audits of the data provided in the Monthly and Annual progress reports submitted by the Contractor and to comment on the accuracy and comprehensiveness of such reports;

- To comment on the quality of the Contractor’s records and audit trails;

- To assess the Contractor’s compliance with the Performance Standards and the Environmental Management Plan;

- To comment on the reliability of the Plant and adequacy of the Contractor’s maintenance procedures;

- To review the adequacy of the training plans of the Contractor and to identify where additional training is needed;

- To review any complaints received from the public in respect of the operation of the wastewater treatment facility;

- To review financial management practices of the Employer and the Employer’s Representative;

- To make recommendations for improvements in the Contractor’s management or operation of the Operation Service;

- To make recommendations for improvements in the Employer’s management and oversight of the Contract;

- To prepare a draft annual performance report for discussion with the Parties;

- To prepare a final annual performance audit report.

The draft and final annual performance reports shall be submitted simultaneously to the Contractor and Employer’s Representative.

# 11.	Standards and codes

The following is a list of acceptable standards and codes which shall be adopted by the Contractor in the design, execution and operation of the Works in addition to ISO 9001:2015 and ISO 45001:2018. The Employer may accept other comparable codes and standards provided that they are widely accepted internationally.

- Civil and Building

| Number | Title |
| --- | --- |
| BS 6399-1:1996 | Loading for buildings. Code of practice for dead and imposed loads (AMD 13669) |
| BS 6399-2:1997 | Loading for buildings. Code of practice for wind loads (incorporating amendment No. 1 and corrigendum No. 1) (corrected and reprinted June 2002) |
| BS 8110-1:1997 | Structural use of concrete. Code of practice for design and construction (AMD 5917) (AMD 6276) (AMD 7583) (AMD 7973) |
| BS 4449:2005 | Steel for the reinforcement of concrete - Weldable reinforcing steel - Bar, coil and recoiled product – Specification |
| BS 8007:1987 | Code of practice for design of concrete structures for retaining aqueous liquids |
| BS 8004:1986 | Code of practice for foundations |
| BS 8666:2005 | Scheduling, dimensioning, bending and cutting of steel reinforcement for concrete - Specification (incorporating Amendment No.1) |
| CP 2012-1:1974 | Foundations for machinery. Foundations for reciprocating machines (AMD 1741) (AMD 1938) |
| BS 6399-3:1988 | Loading for buildings. Code of practice for imposed roof loads (AMD 6033) (AMD 9187) (AMD 9452) |
| BS 5950-1:2000 | Structural use of steelwork in building. Code of practice for design - Rolled and welded sections (AMD Corrigendum 13199) (AMD 17137) (incorporating Corrigendum No. 2) |
| BS 5950-5:1998 | Structural use of steelwork in building. Code of practice for design of cold formed thin gauge sections (AMD 16502) |

- Earthworks

| Number | Title |
| --- | --- |
| BS 1377 | Methods of test for soils for civil engineering purposes |
| BS 6906 | Methods of tests for geotextiles |
| BS 812 | Testing Aggregates |

- Concrete

| Number | Title |
| --- | --- |
| ASTM C31 | Standard Practice for Making and Curing Concrete Test Specimens in the Field |
| ASTM C39 | Standard Test Method for Compressive Strength of Cylindrical Concrete Specimens |
| ASTM C143 | Standard Test Method for Slump of Hydraulic-Cement C Concrete |
| ASTM C1064 | Standard Test Method for Temperature of Freshly Mixed Hydraulic- Cement Concrete |
| BS 6100 | Glossary of Building and civil engineering terms |
| BS EN 932-1 | Tests for general properties of aggregates. Methods for sampling |
| BS EN 932-2 | Tests for general properties of aggregates. Methods for reducing laboratory samples |
| BS EN 12350-1 | Method of sampling fresh concrete in site |
| BS EN 12350-2 | Testing fresh concrete. Slump-test |
| BS EN 12390-1 | Shape, dimensions and other requirements for specimens and moulds |
| BS EN 12390-2 | Making and curing specimens for strength tests |

- Liquid retaining structures

| Number | Title |
| --- | --- |
| BS 8007 | Code of Practice for Design of concrete structures for the retaining of aqueous liquids. |

- Mechanical and Electrical

| Number | Title |
| --- | --- |
| BS ISO 10816, Part 1, Part 3 and Part 7 | Mechanical vibration in rotating and reciprocating machinery. |
| ANSI - HI 1.1-1.2 | - Rotodynamic (Centrifugal) Pumps for Nomenclature and Definitions |
| ASTM A53/A53M | - Standard Specification for Pipe, Steel, Black and Hot Dipped, Zinc-Coated, Welded and Seamless |
| BS EN545 | - Ductile iron pipes, fittings, accessories and their joints for water pipelines. Requirements and test methods |
| BS EN 593 | Industrial valves. Metallic butterfly valves |
| BS EN 598 | - Ductile iron pipes, fittings, accessories and their joints for sewerage applications. Requirements and test methods |
| BS EN ISO 9906 | - Rotodynamic pumps. Hydraulic performance acceptance tests. Grades 1, 2 and 3 |
| BS EN 10088 type 1.4401 or 1.4436 | - Stainless steel 316 low carbon type |
| BS EN 10088 type 1.4306 or 1.4307 | Stainless steel 304 |
| ISO 2531 | - Ductile iron pipes, fittings, accessories and their joints for water applications |
| BS EN 1452 | Plastic piping systems for water supply (UPVC) |
| ISO 4427 | Plastics piping systems - Polyethylene (PE) pipes and fittings for water supply |
| IEC | International Electro Technical Commission |
| IEE | Wiring Regulations (Seventeen Edition) |
| IEEE | Institute of Electrical and Electronics Engineers |
|  | Maldives Energy Authority – Installation Standard Regulations |

- Protective coatings

| Number | Title |
| --- | --- |
| ASTM D543 | Test Method for Resistance of Plastics to Chemical Reagents |
| ASTM D882 | Test Methods for Tensile Properties of Thin Plastic Sheeting |
| ASTM D4541 | Test Method for Pull Off Strength of Coatings Using Portable Adhesion Testers |

APPENDIX 1: Environmental and Social (ES) Requirements

Table ‎9.2 Construction Stage ESMP

| Aspect | Impacts | Risk Rating | Control in Place |  |  | Method Proposed | Proposed Mitigation Measures | Institutional Responsibility |  | Mitigation Cost (MVR) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Yes | No | Plan |  |  | Implementation | Supervision | Contractor to propose |
| Hire Labour |  |  |  |  |  |  |  |  |  |  |
| Local workers | Low employment opportunity for locals | low |  |  | X | Public advertisement | Advertise publicly to hire local construction work groups | Contractor | MUDRP PMU |  |
| Terms & Conditions | Employing workers who do not understand terms and conditions of work | high | X |  |  | Communication | Communicate employment offer to all workers with the number of work hours, wage rate, overtime, insurance and other benefits | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Employment Contract | Sign employment contract with all construction site workers | Contractor | MUDRP PMU |  |
| Foreign Migrant Workers | Charging recruitment fees | high |  |  | X | Planning | Develop a Foreign Migrant Worker Recruitment Plan and a Foreign Migrant Worker Employment Plan | Comtractor | MUDRP PMU |  |
|  | Foreign migrant workers without visa and work permit | high | X |  |  | Compliance with regulations | Conduct periodic checks to see if all foreign migrant workers employed by the project have proper work visas and work permit cards | Contractor | MUDRP PMU |  |
|  | Bonded labour or forced labour | high |  |  | X | Contract | Include a clause in contract to ensure workers recruited for the project are not required to pay for recruitment and employment | MUDRP PMU | Project Director |  |
|  |  |  |  |  |  | Monitoring | Conduct due diligence on all foreign migrant workers recruited for the project | Consultant | MUDRP PMU |  |
|  | Bonded labour or forced labour Withholding personal identification documents such as passport | high |  |  | X | Contract | Include a clause in contract to ensure that all foreign migrant workers have access to their passport and all identification documents | MUDRP PMU | Project Director |  |
|  |  |  |  |  |  | Safe keeping | Provide safe lockers for documents and valuables | Contractor | MUDRP PMU |  |
|  | Responsible Recruitment |  |  |  |  | Recruitment Audit | Conduct period checks on contracts, salary payment, work visas and recruitment fees | Consultant | MUDRP PMU |  |
| Sourcing of construction materials |  |  |  |  |  |  |  |  |  |  |
| Coral mining | Loss of biodiversity | Low | X |  |  | Inform the contractor | Include a clause in contract to prohibit use of any coral for construction | MUDRP PMU | Project Director |  |
| Sand miming | Beach erosion | Low | X |  |  | Inform the contractor | Include a clause in contract to ensure that all construction materials including sand are sourced in compliance with national laws and regulations | MUDRP PMU | Project Director |  |
|  |  |  |  |  |  | Controls | Sand shall not be sourced from the beach or lagoon of an island | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Monitoring | Maintain evidence of sourcing of construction materials | Contractor | MUDRP PMU |  |
| Import of materials | Introduction of alien species and pests | Low |  |  | X | Due diligence | Check all imported construction materials for alien species and pests to ensure alien species or pests do not get introduced | Contractor | MUDRP PMU |  |
|  | Biosecurity concerns from venomous pests and diseases | Low |  |  | X | Control | Check regularly all procured goods for insects, reptiles or pest activity as detection of pests in egg or larval stage in construction materials is difficult and it can take time for infestation to occur | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Reporting | Report anything suspicious or any biosecurity concern to Ministry of Fisheries, Marine Resources and Agriculture | Contractor | MUDRP PMU |  |
| Site Access & preparation |  |  |  |  |  |  |  |  |  |  |
| Site Access | Injuries and accidents for trespassers | Low |  |  | X | Information | Adequate signage shall be provided on site entrance with project name, implementing agencies, financing agencies, contractor, and contact details | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Information | Safety signage shall be erected with no unauthorized access instructions to keep public away. | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Control measures | Adequate, safe and neat fencing shall be erected to cover the entire perimeter of the STP construction site using cost effective fence materials consisting of chain link fence fabric, concrete post, etc. as specified in the Technical Specifications in order to ensure public are unable to access the site. | Contractor | MUDRP PMU |  |
| Site preparation | Cutting down, uprooting, and digging of trees There are no flora or fauna of significance in the proposed STP site. | Low | X |  |  | Management About 03 banyan trees and 03 coconut palms will be removed. 01 Beef Wood, 01 Lead Tree, and 01 Madras Pine will need to be removed as well | For removal of coconut palms, all root bulb and base of the trunk shall be cut into small pieces and trunk shall be transported to the Waste Management Center to be sold. Parts of the root bulb can be used for backfilling of the depression created. The use of root bulbs for backfilling or grinding the stump of the root bulb will minimize waste generated during site clearance, maintain original soil conditions as well as minimize additional sand needed for filling. | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  |  | For other mature trees branches shall be cut to manageable pieces before transporting to Waste Center | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | For all mature trees and coconut palms removed compulsory replantation shall be implemented | For replantation, first priority shall be given to replant in areas surrounding the STP site. This will serve the dual purpose of acting as a green buffer around STP. | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Records | Evidence of replanting to meet compensatory 1:2 minimal replanting ration requirement shall be documented and maintained for at least twenty years. | MUDRP | MNPHI |  |
|  |  |  |  |  |  | Controls | The cutting or removal of replanted trees shall be strictly controlled for a minimum of twenty years. | HDC | MNPHI |  |
| Physical Cultural Resources | Chance finds No risks to cultural resources as the land is reclaimed land between 1997-2002 | Low | X |  |  | Information |  |  |  |  |
| Accommodation of workers |  |  |  |  |  |  |  |  |  |  |
| Living Conditions | Worker illness and exposure to health hazards | High |  |  | X | Contract provisions | Provide adequate sleeping arrangements for workers | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Safe water | Make available safe water for drinking, cooking and washing at accommodation venue | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Toilet and shower | Adequate toilet and shower facilities shall be provided | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  |  | Provide adequate water supply in all toilets and showers | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Waste collection | Provide garbage bins in the premises and ensure that these are regularly emptied and disposed of in a hygienic manner | Contractor | MUDRP PMU |  |
| Water & electricity supply |  |  |  |  |  |  |  |  |  |  |
| Ground water | Over extraction and pollution of ground water | Low | X |  |  | Ensure water for construction process is sourced from MWSC and according to HDC regulations if any | Do not obtain water for project purposes from any public or community water taps | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  |  | Do not dig wells and do not extract water from the ground without prior permission from the HDC | Contractor | MUDRP PMU |  |
| Health & Safety | Electrocution and safety risks | Low | X |  |  | STELCO | Ensure electricity is supplied from Stelco | Contractor | MUDRP PMU |  |
| Transport of construction materials |  |  |  |  |  |  |  |  |  |  |
| Health & Safety | Accidents and injuries due to over loading and speeding | Low |  |  | X | Controls | Avoid over loading vessels that transport material to construction sites | Contractor PM | Contractor |  |
|  |  |  |  |  |  | Minimize possible public nuisance from dust due to haulage | Transport all sand and aggregate in covered vehicles or materials should be covered with tarpaulin | Contractor PM | Contractor |  |
|  |  |  |  |  |  | Transport management | Ensure vehicle movement is via roads are scheduled to avoid peak traffic hours | Contractor PM | Contractor |  |
|  |  |  |  |  |  |  | Ensure school hours are avoided as much as possible | Contractor PM | Contractor |  |
|  |  |  |  |  |  |  | Ensure transport is at low vehicular speeds | Contractor PM | Contractor |  |
| Public Property | Risk of damage to roads | Low |  |  | X | Controls | Loads should be divided to prevent damages to roads | Contractor PM | Contractor |  |
|  |  |  |  |  |  | Cleaning | Mud patches caused by material transporting vehicles in the access road should be immediately cleaned | Contractor PM | Contractor |  |
|  |  |  |  |  |  | Repair | If there are damages to local roads and other utilities due to hauling in roads attend to repair all damaged infrastructure/ roads | Contractor PM | Contractor |  |
| Storage of construction materials |  |  |  |  |  |  |  |  |  |  |
| Health & Safety | Accidents and injuries | Low |  |  | X | Location control | Conduct all loading and unloading within the site | Contractor PM | Contractor |  |
|  |  |  |  |  |  | Maintain air quality | All construction materials such as sand, cement, metal, etc. should be stored under cover | Contractor PM | Contractor |  |
|  |  |  |  |  |  | Prevent fire hazard and oil spills | High risk materials such as diesel shall be stored in appropriate containers and placed in paved surface | Contractor PM | Contractor |  |
|  |  |  |  |  |  | Prevent spill of paint and chemicals | Containers shall be inspected regularly for leakage | Contractor PM | Contractor |  |
| Excavation and dewatering |  |  |  |  |  |  |  |  |  |  |
| Ground water | Water quality risks Dewatering will be minimal and temporary | Low | X |  |  | Permission | Seek permission from EPA if dewatering is required | Contractor | MUDRP PMU |  |
| General construction |  |  |  |  |  |  |  |  |  |  |
| Pollution control | Risks of litter and pollution | Medium |  |  | X | Waste management | Ensure construction generated waste is adequately segregated | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  |  | Provide segregated recyclable construction materials to Waste Management Center | Contractor PM | Contractor |  |
|  |  |  |  |  |  |  | Transport all remaining construction waste to Thilafushi at the completion of construction | Contractor | MUDRP PMU |  |
| Health & Safety | Accidents, injuries and illnesses | High |  |  | X | Planning | Prepare an Occupational Health and Safety Plan | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Safety measures at site | Safe drinking water shall be made available in sufficient quantity at work site | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  |  | Make readily available a first aid unit including an adequate supply of sterilized dressing materials and first aid supplies at the site office at all times | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  |  | Provide fire extinguishers at project site | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Information & signage | Put up signage with instructions on first aid management and emergency operational procedures in Dhivehi language | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  |  | Prepare a sign board with names and contact information for emergency services such as ambulance, hospitals, police and the fire services and display at the work site. | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  |  | All workers should be provided with health and safety information appropriate to the work that they undertake | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Training | Conduct onsite safety training for all labourers during the ESMP training prior to the start of construction activities | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  |  | Provide training to labourer’s on the risks of working in a tropical open project site | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  |  | Provide adequate training and guidance to all workers on prevention of accidents involving human beings, vehicles, machinery or accidents during construction period | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Insurance | Obtain insurance to compensate for any damages, injuries caused to laborers during the construction period | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Personal Protective Equipment | All workers should be provided with safety gear and personal protective equipment at all times. This includes: safety hats, helmets, safety goggles, safety belts, boots, ear plugs, masks and gloves | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  |  | Protective footwear and protective goggles should be used by all workers employed on mixing of materials like cement, concrete etc | Contractor PM | Contractor |  |
|  |  |  |  |  |  |  | Ear muffs/ear plugs shall be used by workers if workers are to be exposed for high noise levels for extended periods of time and workers undertaking crushing, compaction, or concrete mixing operations | Contractor PM | Contractor |  |
|  |  |  |  |  |  |  | Welder’s protective eye-shields shall be used by workers who are undertaking welding work | Contractor PM | Contractor |  |
|  |  |  |  |  |  |  | Protective gloves shall be used by workers handling any construction related chemicals | Contractor PM | Contractor |  |
|  |  |  |  |  |  |  | Maintain an adequate stock of gloves, ear muffs, goggles, dust masks, safety harness and any other equipment considered necessary at site office | Contractor PM | Contractor |  |
|  |  |  |  |  |  | Risk reduction | Special precaution must be undertaken to ensure workers are safe from risk of electrocution. No open electrical wiring or cables shall be kept on site | Contractor PM | Contractor |  |
|  |  |  |  |  |  | Communication | All communication to workers shall be presented in the local languages and in the case of migrant workers in their local language as well. | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Emergency transport | Ensure availability of suitable transport at all times to take injured or sick person(s) to the nearest hospital | Contractor PM | Contractor |  |
|  |  |  |  |  |  | Monitoring | Prepare a safety inspection checklist taking into consideration what the workers are supposed to be wearing and monitor and record monthly | Contractor | MUDRP PMU |  |
|  | Management of COVID19 | High |  |  | X | COVID19 prevention | Travel permit must be taken from HPA for the workers if traveling from Male’ or an island placed under COVID19 monitoring. The standard quarantine procedure must be followed as instructed by the authorities. Workers must be briefed about the safety protocols and social distancing measures that has to be enforced. The workers must perform frequent hand hygiene. All workers must wear face masks. The movement of workers must be restricted between the labor camp and work site as much as possible. Daily body temperature of all the workers should be taken and log records maintained. If a worker is having a temperature of 37.8C or above or symptoms of flu that person must not report to work and should be self-isolated and respective authorities notified. Handwashing or hand sanitizing facilities must be established at the work site and the labor camp. Labor camp should facilitate social distancing. The beds should be kept at least 3 – 6 fts apart. COVID19 awareness materials should be displayed in the worksite and the labor camp. Construction tools should be cleaned using disinfecting solution (1:9 bleach solution) at the end of each day or when changing shifts (if shift-based work methodology is adopted). | Contractor | MUDRP PMU |  |
|  | Onsite Resting and Sanitary Arrangements |  |  |  | X | Toilet Facilities in Construction Site | The contractor should identify a toilet that the works can access within 5 mins from the project. This could be via renting a toilet from a nearby utility area / office building / house, installing portable toilets or by making back and forth transport readily available to the accommodation building | Contractor | MUDRP PMU |  |
| Decent Work | Long work hours | High | X |  |  |  | Worker shall not be forced to work for more than 48 hours per week | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  |  | Worker shall not be made to work for more than 6 days a week consecutively without providing 24 hours for rest | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  |  | Worker shall not be made to work continuously for more than 5 hours without providing a break for at least 30 minutes |  |  |  |
|  | Withholding wages | High | X |  |  | Regulatory compliance | Salary should be paid to all permanent contract workers once a month | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Bank Accounts | Salary shall be deposited directly to bank accounts of all contract workers | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Records | A salary slip that with separate itemization for number of hours worked, overtime, payments, and any deductions shall be provided to each worker | Contractor HR Manager | Contractor |  |
|  |  |  |  |  |  | Controls | All temporary staff for day work should be paid on a daily basis | Contractor HR Manager | Contractor |  |
|  | Inadequate water and food for workers | High |  |  | X | Water supply | Supply sufficient quantity of potable water in every workplace and work site at suitable and easily accessible places | Contractor HR Manager | Contractor |  |
|  |  |  |  |  |  | Water quality tests | Regular maintenance of such provisions and checks on water quality | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Food | Minimum 03 meals shall be provided to construction staff per day | Contractor HR Manager | Contractor |  |
|  |  |  |  |  |  | Break times | Appropriate meal break time shall be provided | Contractor HR Manager | Contractor |  |
| Site closure & Demobilization |  |  |  |  |  |  |  |  |  |  |
| Health & Safety | Site not ready for operations | Low |  |  | X | Remove materials and equipment | Remove all excess material, equipment, vehicles from the project site prior to complete demobilization | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Dismantle temporary buildings | Dismantle all temporary site offices and remove from the site | Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Repair damages | If the storage site has been dilapidated in any way as per the evaluation of the engineer, reinstate it to the original condition prior to demobilization | Contractor | MUDRP PMU |  |

Table ‎9.3 Operation Stage ESMP

| Aspect | Impacts | Risk Rating | Control in Place |  |  | Method Proposed | Proposed Mitigation Measures | Institutional Responsibility |  | Mitigation Cost (MVR) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Yes | No | Plan |  |  | Implementation | Supervision |  |
| Influent Quality | Interruptions to sustainable operation of STP due to quality of influent | High |  |  | X | Stakeholder consultation | Conduct stakeholder consultations to determine measures necessary to ensure influent control | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Develop guidance | Develop guidelines for influent control | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Public consultation | Undertake public consultation on influent control measures | HDC/MWSA | MUDRP PMU |  |
|  |  |  |  |  |  | Information campaign | Disseminate information on influent control measures | HDC | MUDRP PMU |  |
| Renewable Energy | Increase in greenhouse gas emissions | High |  |  | X | Renewable energy | Install adequate roof top solar PV for STP | RE Contractor | MUDRP PMU |  |
|  | Risk of plant disruption due to electricity failure | High |  |  | X | Back up power | Stand-alone back-up generator shall be installed in the STP location to address plant disruption from electricity failure and the consequent impairment of the biological treatment system and odour control | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Warning system | Alarm and warning systems shall be included to monitor any power failures and highlight when site inspections are required to assess the situation. | DBO Contractor | MUDRP PMU |  |
| Odour control | Public health impacts and nuisance from foul odour | High |  |  | X | Strategy & plan | Develop an Odour Control and Management Plan | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Design controls | Ensure the STP is totally enclosed | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Control measures | Cover, extract, and vent all of the tanks and other STP components | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Control measures | Negative pressure ventilation shall be provided within the enclosures to avoid any odorous emissions from the STP | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Control measures | Inlet screens, sewage channels and screening bins; sludge holding tanks; and equipment with potential odour shall be covered and ventilated | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Control measures | Adequate mixing and aeration shall be provided at equalization and sludge holding tanks to prevent sewage septicity | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Control measures | Chemical or biological deodorization facilities with at least 99.5% odour removal efficiency shall be provided to treat potential odorous emissions from the STP including sewage channels / tanks, and screening facilities so as to minimize any potential odour impact to the nearby sensitive receptors. Suitable odour treatment such as 2 stage biotrickling filter/activate carbon system or wet chemical scrubber, and UV disinfection shall be considered. | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Control measures | The deodorisation shall be designed such that the discharge is directed away from sensitive receptors. | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Consultation | If a point source stack discharge is to be erected Department of Civil Aviation shall be consulted on the height of the stack due to the close proximity of the Velana International Airport sea plane operations. | MUDRP PMU | Project Director |  |
|  |  |  |  |  |  | Control measures | The odour control unit shall be designed to eliminate the risk of equipment failure and will allow periodic scheduled maintenance to be undertaken. Measures will be undertaken to avoid and minimise residual odours during maintenance works. | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Monitoring and audit | Odour surveys and odour assessments shall be conducted regularly. Periodic assessments shall compare actual odour emissions against emission rates used in the design of technology and STP. These assessments shall determine whether odour emissions cause any environmental nuisance beyond the site of the STP during different weather conditions | STP Operator | HDC |  |
|  |  |  |  |  |  | Monitoring and audit | Maintain an Odour Complaints Register. All odour related complaints shall be recorded on an Odour Complaints Register | STP Operator | HDC |  |
|  |  |  |  |  |  | Monitoring and audit | Odour complaints shall be reported annually to EPA as part of the Annual Environmental and Social Monitoring | STP Operator | HDC |  |
| Effluent Management | Impacts from discharge of effluents | Low | X |  |  | Strategy & Plan | Develop a Treated Wastewater Discharge Management Plan and an. The Marine Treated Wastewater Discharge Management Plan must address marine water quality; marine habitat impacts; and trigger points which determine when appropriate remedial actions are required. | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Monitoring | Develop a Marine Habitat Monitoring and Management Plan | Consultant | MUDRP PMU |  |
|  |  |  |  |  |  | Alternatives | Consider alternative methods of managing the significant volume of treated wastewater effluent from the STP | HDC, MWSC | MUDRP PMU |  |
| Sludge Management | Volume of sludge will keep growing with the operation of STP | High |  |  | X | Plan & strategy | Develop sludge management plan | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Facility | Develop the facility for composting of sludge | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Business plan | Develop business plan for sludge management | HDC | MUDRP PMU |  |
| Waste Management | Impacts from screened solids, oil and grease and general waste | High | X |  |  | Strategy & plan | Develop a waste management plan with clear roles and responsibilities | DBO Contractor | MUDRP PMU |  |
| Pest Control | Vectors such as mosquitoes and cats and rodents | Med |  |  | X | Strategy & plan | Develop a pest control and management plan for STP site | DBO Contractor | MUDRP PMU |  |
| Noise Management | Vibration and noise from equipment, machinery and pumps. | Low |  |  | X | Control measures | Equipment and machinery will be run as efficiently as possible and run only when the required load is reached | STP Operator | Utility Regulator |  |
|  |  |  |  |  |  | Scheduling | Limit the time of use of equipment and machinery to specified working hours between 9.00 am and 6.00 pm | STP Operator | Utility Regulator |  |
|  |  |  |  |  |  | Repair and maintenance | Service the equipment regularly to ensure they are in best condition for use | STP Operator | Utility Regulator |  |
| Fire Safety | Risks to equipment and facility from fire accidents | Low |  |  | X | Information | Put up signage to ensure flammable liquids are not permitted on STP site, do not get accepted and get stored at STP site | STP Operator | Utility Regulator |  |
|  |  |  |  |  |  | No-smoking | Enforce strictly “no-smoking” at STP site | STP Operator | Utility Regulator |  |
|  |  |  |  |  |  | Staffing | Ensure a minimum of one staff at STP at all hours to prevent deliberate arson | STP Operator | Utility Regulator |  |
|  |  |  |  |  |  | Information | Put up signage showing relevant contact numbers for MNDF, Police and emergency services in a location readily visible for staff | STP Operator | Utility Regulator |  |
|  |  |  |  |  |  | Equipment | Place a Water 9Ltr fire extinguisher with Cabinet and a CO2 2KG with Cabinet in the compost area | STP Operator | Utility Regulator |  |
|  |  |  |  |  |  | Equipment | Procure a pressure pump and keep within the STP site and provide the necessary training | STP Operator | Utility Regulator |  |
|  |  |  |  |  |  | Training | Train staff on use of fire extinguishers, fire safety practices and make them aware of the location of fire safety equipment | STP Operator | STP Operator |  |
| Security |  | Med | X |  |  | Facility | Erect a wall and high fence along boundaries of STP | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Facility | Install a lockable gate | DBO Contractor | MUDRP PMU |  |
|  |  |  |  |  |  | Equipment | Ensure gate of STP is closed outside work hours | STP Operator | Utility Regulator |  |
|  |  |  |  |  |  | Information | Put up signage to ensure the safety of visitors | DBO Contractor | MUDRP PMU |  |
| Work visa | Foreign migrant workers without visa and work permit | High | X |  |  | Compliance with regulations | Ensure all foreign migrant workers have proper work visas and work permit cards | STP Operator | Utility Regulator |  |
| Charging recruitment fee from migrant workers | Bonded labour or forced labour | High |  |  | X | Contract | Ensure workers recruited for the project are not required to pay for recruitment and employment | STP Operator |  |  |
|  |  |  |  |  |  | Monitoring | Conduct due diligence on all foreign migrant workers recruited for the project | STP Operator |  |  |
| Withholding personal identification documents such as passport | Bonded labour or forced labour | High |  |  | X | Contract | Ensure that all foreign migrant workers have access to their passport and all identification documents | STP Operator |  |  |
|  |  |  |  |  |  | Safe keeping | Provide safe lockers for documents and valuables | STP Operator |  |  |
| Decent Work | Long work hours | High | X |  |  |  | Worker shall not be forced to work for more than 48 hours per week | STP Operator |  |  |
|  |  |  |  |  |  |  | Worker shall not be made to work for more than 6 days a week consecutively without providing 24 hours for rest | STP Operator |  |  |
|  |  |  |  |  |  |  | Worker shall not be made to work continuously for more than 5 hours without providing a break for at least 30 minutes | STP Operator |  |  |
|  | Withholding wages | High | X |  |  | Regulatory compliance | Salary should be paid to all permanent workers once a month | STP Operator |  |  |
|  |  |  |  |  |  | Bank Accounts | Salary shall be deposited directly to bank accounts of all workers | STP Operator |  |  |
|  |  |  |  |  |  | Records | A salary slip that with separate itemization for number of hours worked, overtime, payments, and any deductions shall be provided to each worker | STP Operator |  |  |

Appendix 2: Financial Memorandum

Article 1

Purpose

- The purpose of this Memorandum is to outline financial arrangements for the design, execution and operation of the Sewerage Treatment Plant including the provisions of the Asset Replacement Fund.

Article 2

The Project

The project includes the Design, Build and Operations for a 10 MLD sewage treatment plant for Hulhumalé Phase 1 with expected population of 80,000. In addition to the above, the project includes design, procurement, installation and commissioning of In-Vessel Sludge Composting Plant for treatment of sludge produced at the STP and Installation and commissioning of Odour Control System for the STP. Design and Build is expected to be completed in 24 months and DBO Contractor’s Operations and Maintenance period will be 10 years.  Details of the project are outlined in the RFP document Part 2 Employers Requirements.

Article 3

Asset Transfer

Once the Design Build is completed the Sewage Treatment Plant including all responsibility of monitoring the Contractor during operations and maintenance period will be transferred to the Male Water and Sewerage Company (MWSC).

Article 4

Financing Arrangements

The project consists of three stages namely Design stage, Build stage and Operations Stage. Design stage includes the formulation of detail design. Build stage will include the construction/civil works. Operations stage will include the operations and maintenance of the facility once it’s commissioned.  The design and construction stage will be financed by World Bank through the Maldives Urban Development and Resilience Project (MUDRP).

Payments to the DBO contractor will be made via the Project Management Unit (PMU) of MUDRP established in the Ministry of National Planning Housing and Infrastructure upon submission of invoices for interim payments and approval of the same. The payment for the DBO contractor during the Operations and Maintenance period including the Asset Replacement Fund in accordance with the Asset replacement Schedule will be undertaken by the MWSC.

Site Plans / Concept Drawings

Supplementary Information

Feasibility Study, Conceptual Designs and Bidding Documents for Design, Build and Operate Contract for Establishing STP in Hulhumalé Report.

PART 3 – Conditions of Contract and Contract Forms

Gold Book:

© FIDIC 2008. All rights reserved.

The Conditions of Contract are the “General Conditions” which form part of the “Conditions of Contract for Design, Build and Operate Projects first edition 2008” published by the Federation Internationale Des Ingenieurs – Conseils (FIDIC and the following “Particular Conditions” which comprise of the World Bank’s COPA and the amendments and additions to such General Conditions.

An original copy of the above FIDIC publication i.e. “Conditions of Contract for Design, Build and Operate Projects” must be obtained from FIDIC.

International Federation of Consulting Engineers (FIDIC)

FIDIC Bookshop – Box- 311 – CH – 1215 Geneva 15 Switzerland

Fax:  +41 22 799 49 054

Telephone:  +41 22 799 49 01

E-mail:  fidic@fidic.org

www.fidic.org

FIDIC  code: ISBN13: 978-2-88432-052-8

Section VIII – General Conditions (GC)

Section IX – Particular Conditions (PC)

The following particular conditions shall supplement the General Conditions. Whenever there is a conflict, the provisions herein shall prevail over those in the General Conditions.

Particular Conditions of Contract

Part A – Contract Data

| Conditions | Sub-Clause | Data |
| --- | --- | --- |
| Where the Contract allows for Cost Plus Profit, percentage profit to be added to the Cost: | 1.1.24 | Not applicable |
| Cut-Off Date (number of days after the Time for Completion of Design-Build): | 1.1.26 | 90 Days |
| Contractor’s Key Personnel names | 1.1.21 & 6.9 | Name of Contractor’s Key Personnel will be entered in the below during preparation of the Contract Agreement Sl.; Name; Position; Experience (Yr). 1.. 2.. 3.. 4.. |
| Employer’s Representative’s name and address: For the Design Build Period: For the Operation Service Period: | 1.1.35 | Name: Fathimath Shaana Farooq Designation: Project Director Address: Ministry of National Planning, Housing and Infrastructure Name: Mohamed Faisal Designation: Assistant General manager, Waster Water & Networks Address: Male Water and Sewerage Company |
| Parts of the Works that shall be designated a Section for the purposes of the Contract: | 1.1.70 | None |
| Time for Completion of Design-Build: | 1.1.78 | 24 months from date of commencement |
| Borrowers Name: | 1.1.85 | Republic of Maldives |
| Agreed methods of electronic transmission: | 1.3 | Electronic mail (E-mail) |
| Address of Employer for communications: | 1.3 | Project Director Maldives Urban Development and Resilience Project Ministry of National Planning, Housing and Infrastructure Ameenee Magu, Male Maldives mudrp@planning.gov.mv |
| Address of Employer’s Representative for communications: For the Design Build Period: For the Operation Service Period: | 1.3 | Project Director Maldives Urban Development and Resilience Project Ministry of National Planning, Housing and Infrastructure Ameenee Magu, Male Maldives mudrp@planning.gov.mv Male Water and Sewerage Company |
| Address of Contractor for communications: | 1.3 | TBD |
| Governing law: | 1.4 | Law of the Republic of Maldives |
| Ruling language: | 1.4 | English |
| Language for communications: | 1.4 | English |
| Time for the Parties to sign a Contract Agreement | 1.6 | 28 days after receipt of the Letter of Acceptance |
| Joint and Several Liability: Type and minimum amounts of paid up share capital required: Minimum shareholding requirement after lock-in period: | 1.15 | Not Applicable |
| Time for access to the Site: | 2.1 | “No later than the Commencement Date” |
| Employer approval not required for variations less than: | 3.1 | Employer approval is required for all variations |
| Performance Security: | 4.2 | The Performance Security will be in the form of a “demand guarantee” in the amount(s) of 7 percent of the Accepted Contract Amount for the Design Build and in the same currency (ies) of the Accepted Contract Amount. |
| Reduction in Performance Security at the end of the Retention Period: Further reduction in Performance Security following five consecutive years of Operation Service during which the Contractor has achieved full compliance with the standards specified in the Schedule of Performance Standards | 4.2 | The Performance Security will be in the form of a “demand guarantee” in the amount(s) of 8 percent of the Accepted Contract Amount for the Design Build and in the same currency (ies) of the Accepted Contract Amount. The Employer may release full or part of the Performance Security proportionately for the Design Build Works for which the Contractor has received a Completion Certificate. The Performance Security will be in the form of a “demand guarantee” in the amount(s) of 4 percent of the Accepted Contract Amount for the Design Build and in the same currency (ies) of the Accepted Contract Amount. The Employer may also release proportionately the Performance Security against Operation Services during which the Contractor has received a certificate of full compliance with the Performance Standards |
| Environmental and Social (ES) Performance Security: ES Performance Security Required: Amount and type of the ES Performance Security: | 4.2 | Yes The ES Performance Security will be in the form of a “demand guarantee” in the amount(s) of 3% of the Accepted Contract Amount for the Design Build and in the same currency (ies) of the Accepted Contract Amount. |
| Period for notification of errors, faults and other defects: | 5.1 | 56 Days |
| Normal working hours on the Site: | 6.5 | As per Labor law of republic of Maldives |
| Period of the Operation Service: | 8.2 | [120 ] months |
| Time for Completion of Design-Build: | 9.2, 1.1.78 | [24] months, sectional completion not applicable |
| Time for Completion of each Section: | 9.2, 1.1.78 | [24 ] months Not applicable |
| Delay damages payable for each day of delay | 9.6 | 0.1% of the Accepted Contract Amount for Design-Build, less provisional sum for DAB |
| Maximum amount of delay damages | 9.6 | 10% of the Accepted Contract Amount less provisional sum for DAB. |
| Commencement Date if different from PC 10.2. | 10.2 | Not Applicable |
| Maximum amount of Performance Damages payable by the Contractor (Operation Service): | 10.6 and 10.7 | 50% of the contract Amount for Operation Services |
| Maximum amount of compensation payable by Employer (Operation Service): | 10.6b | Not Applicable |
| Maximum amount of performance damages payable by the Contractor in any contract year during the Operation Service Period: | 10.6 and 10.7 | 50% of the contract Amount for Operation Services |
| Rights of the Employer if the failure continues for more than 84 days: | 10.7 | As per Clause 10.7 |
| Percentage rate to be applied to Provisional Sums for overhead charges and profits: | 13.5 | Not Applicable |
| Contract Price and Rates and Prices to be adjusted for changes in cost as further detailed in the Schedule of Cost Indexation: a) Design-Build b) Operation Service (excluding Asset Replacement) c) Asset Replacement | 13.8 | Not Applicable a) No b) Yes c) Yes |
| Amount of Advance Payment | 14.2 | 15% of the Accepted Contract Amount for the Design Build payable in the currencies and proportions in which the Accepted Contract Amount for Design Build is payable against an unconditional Bank Guarantee. |
| Percentage deductions for the repayment of the Advance Payment: | 14.2 | a) Advance payment recovery shall be 20% from each interim payment until the full recovery of the advance payment. |
| Requirements for submission of Statements if different from the GC and PC: | 14.3 | Same as GC |
| Percentage of Retention: | 14.3 | 5% of the total Contract Amount |
| Limit of Retention Money: | 14.3 | As per the Schedule of Payment |
| Plant and Materials for payment when shipped: | 14.6(b)(i) | Not Applicable |
| Plant and Materials for payment when delivered to the Site: | 14.6(c)(i) | Applicable |
| Minimum Amount of Interim Payment Certificate applicable for the Design-Build. Minimum Amount of Interim Payment Certificate applicable for the Operation Service. | 14.7(b) | Per month minimum 1% of the Contract Amount for Design-Build Works Per month 1% of the Contract Amount for the Operation Service |
| Currencies for payment of Contract Price: [or reference Schedule of Payments] | 14.17 | United States Dollars |
| Proportions of Local and Foreign Currencies are: [or reference Schedule of Payments] | 14.17 | Not Applicable |
| Rate of Exchange [or reference Schedule of Payments] | 14.17 | Rate of exchange will be the exchange rate of the Central Bank of Maldives( MMA) on the date of submission |
| Currencies of Payment of damages shall be: During the Design-Build During the Operation Service: | 14.17 | United States Dollars (USD) United States Dollars (USD) |
| Amount of Maintenance Retention Fund: | 14.19 | Maintenance Retention Fund shall be created by deducting five percent (5%) from the value of each interim payment |
| Operation of forces of nature allocated to the Contractor: | 17.1 b (iii) |  |
| Total liability of the Contractor shall not exceed: | 17.8 | 120% of total contract price |
| Permitted deductible limits: | 19.2(a)(i) | 5% of the Contract Amount for Design-Build Period |
| Additional sum to be insured: | 19.2(a)(ii) | 15% |
| Employer’s Risks to be insured if different to Sub-Clause 17.1: | 19.2(a)4 | Same as GC |
| Exceptional Risks to be insured if different to Sub-Clause 18.1: | 19.2(a)5 | Same as GC |
| Insurance of Contractor’s Equipment (minimum amount required): | 19.2(b) | 100% of the value |
| Minimum amount of professional liability insurance required: | 19.2(c) | 2.5% of Design-Build Contract Price |
| Period for which professional liability insurance required: | 19.2(c) | Entire period the DBO contract |
| Minimum amount of insurance required for injury to persons and damage to property: | 19.2(d) | USD 1,000,000 |
| Other insurances required from the Contractor (give details): | 19.2(f) | All risk insurance, third parties insurance, motor vehicles, worker’s compensation and other the Contract may require |
| Minimum amount of fire extended cover insurance required: | 19.3(a) | USD 1,000,000 |
| Minimum amount of insurance required to cover injury to any person and damage to property: | 19.3(b) | USD 1,000,000 |
| Other insurances required by law from the Contractor (give details): | 19.3(d) | NOT REQUIRED |
| Other optional insurances required from the Contractor (give details): | 19.3(e) | NOT REQUIRED |
| Time for appointment of DAB member(s): | 20.3 | 42 days after signature by both parties of the Contract Agreement. |
| The DAB shall be comprised of: | 20.3 | One sole Member |
| List of proposed members of DAB | 20.3 | None |
| Appointment (if not agreed) to be made by: | 20.4 | As per Arbitration Act of Maldives ( Act no: 10/2013) |
| Rules of arbitration: | 20.8 (a) | As per Arbitration Act of Maldives ( Act no: 10/2013) |
| Place of arbitration | 20.8 (a) | # Singapore |

Table: Summary of Sections

| Section Name/Description (Sub-Clause 1.1.70) | Time for Completion of Design Build (Sub-Clause 1.1.78) | Damages for Delay (Sub-Clause 9.6) |
| --- | --- | --- |
| Not Applicable |  |  |

Particular Conditions of Contract

Part B- Special Provisions

| Sub-Clause 1.1.11 |  | Contract Agreement: “if any” is deleted. |
| --- | --- | --- |
| Sub-Clause 1.1.21 |  | Contractor’s Personnel The following is added at the end of the sub-clause: “Contractor’s Personnel includes Key Personnel included in the Contract.” |
| Sub-Clause 1.1.49 |  | Letter of Tender After “entitled letter of tender”, “or letter of Proposal” is added. |
| Sub-Clause 1.1.72 |  | Site After “are to be executed”, “, including storage and working areas,” is added. |
| Sub-Clause 1.1.84 to 1.1.93 are added after Sub-Clause 1.1.83 |  |  |
| Sub-Clause 1.1.84 |  | “Bank” means The International Bank for Reconstruction and Development and/or the International Development Association (whether acting on its own account or in its capacity as administrator of trust funds provided by other donors. |
| Sub-Clause 1.1.85 |  | “Borrower” means the borrower or recipient of Bank’s Investment Project Financing (IPF) identified in the Contract Data. |
| Sub-Clause 1.1.86 |  | “ES” means Environmental and Social (including Sexual Exploitation and Abuse (SEA) and Sexual Harassment (SH)). |
| Sub-Clause 1.1.87 |  | “Sexual Exploitation and Abuse” “(SEA)” means the following: Sexual Exploitation is defined as any actual or attempted abuse of position of vulnerability, differential power or trust, for sexual purposes, including, but not limited to, profiting monetarily, socially or politically from the sexual exploitation of another. Sexual Abuse is defined as the actual or threatened physical intrusion of a sexual nature, whether by force or under unequal or coercive conditions; and “Sexual Harassment” “(SH)” is defined as unwelcome sexual advances, requests for sexual favors, and other verbal or physical conduct of a sexual nature by the Contractor’s Personnel with other Contractor’s or Employer’s Personnel. |
| Sub-Clause 1.1.88 |  | “Existing Facilities” means the existing plant, equipment, buildings and other assets at the Site to be taken over and operated by the Contractor as further described in the Employer’s Requirements. |
| Sub-Clause 1.1.89 |  | “Performance Standards” means the standards to be achieved by the Contractor during the Operations Period and includes the standards specified in the Schedule of Performance Standards. |
| Sub-Clause 1.1.90 |  | “Schedule of Performance Standards” means the schedule attached to the Contract Agreement specifying the core output Performance Standards to be achieved by the Works and the Contractor at commissioning and during the Operation Service Period. |
| Sub-Clause 1.1.91 |  | “Schedule of Performance Damages” means the schedule attached to the Contract Agreement which specifies the amounts of damages payable by the Contractor in respect of a breach of the standards specified in the Schedule of Performance Standards. |
| Sub-Clause 1.1.92 |  | “Influent” means the untreated water/ wastewater entering the Works at the delivery point to the Works). |
| Sub-Clause 1.1.93 |  | “Influent Baseline” means the quality characteristics of the untreated Influent as set out in the Employer Requirements, used as the baseline for the design of the Works.” |
| Sub-Clause 1.2 |  | 1.2 Interpretation The following is added as a new sub- clause: Unless inconsistent with any provision of the Contract, the meaning of any trade term and the rights and obligations of the Parties thereunder shall be prescribed by Incoterms. Incoterms means international rules for interpreting trade terms published by the International Chamber of Commerce (latest edition), 38 Cours Albert 1er, 75008 Paris, France. |
| Sub Clause 1.2(g) |  | Tender The following is added as a new sub-clause: (e) “the word “tender” is synonymous with “Proposal” and “tenderer” with “Proposer” and the words “tender documents” with “request for proposal documents”. |
| Sub-Clause 1.3 |  | Communications In the third line “, discharges” is added after “requests.” |
| Sub-Clause 1.4 |  | Law and Language the whole Sub-Clause is replaced with the following in its entirety: “1.4 Law and Language The second sentence is deleted and replaced by: “The ruling language of the Contract shall be that stated in the Contract Data.” |
| Sub-Clause 1.5 |  | Priority of Documents The following documents are added in the list of Priority Documents after (e): “(f) the Particular Conditions Part C- Fraud and Corruption; (g) the Particular Conditions Part D- Environmental and Social (ES) Metrics for Progress Reports;” and the list renumbered accordingly. |
| Sub-Clause 1.6 |  | Contract Agreement in the second line “unless they agree otherwise” is replaced with “unless the Particular Conditions establish otherwise.” |
| Sub-Clause 1.7 |  | Operating License The first paragraph is deleted and replaced with the following: “In consideration of the Contractor’s performance of the Operation Service, from the date of commencement of the Operation Service the Employer grants to the Contractor for the Operation Service Period, the exclusive right, license and authority to occupy, use and enjoy the Site free of charge and free and clear of all claims for the purposes of carrying the Operation Services. Together with the Letter or Acceptance, the Employer shall, where necessary, issue, or cause to be issued, to the Contractor the Operating License or equivalent legal authorization to enable the Contractor to operate and maintain the Works during the Operation Service Period.” This Operating License shall come into full force and effect upon the issue of the Commissioning Certificate required under Clause 11.7 and shall remain in force during the Operation Service Period.” |
| Sub-Clause 1.8 |  | Assignment The whole sub-clause is replaced with the following: “(a) Except as provided in (b), (c) and (d) below, neither Party shall assign the whole or any part of the Contract or any benefit or interest in or under the Contract without the consent of the other Party. (b) The Contractor may as security in favour of a bank or financial institution, assign its right to any monies due, or to become due, under the Contract. (c) During the Operation Service Period, the Employer may assign the whole of the Contract to the agency, if any, specified in the Contract Data subject to the following: - The Employer shall provide at least 90 days’ written notice to the Contractor of its intention to assign the Contract. Such notice shall specify the financial arrangements that have been made for payment of the Contract Price to the Contractor. - The Employer shall not assign the Contract until reasonable evidence has been provided to the Contractor that financial arrangements have been made, and will be maintained, which will enable the agency to pay the Contract Price punctually. (d) Where the Contractor is composed of a joint venture, no joint venture member shall assign or novate its interest in the Contract or the joint venture until the second anniversary of the date of the Commissioning Certificate. Following the second anniversary of the issue of the Commissioning Certificate a joint venture party that is not the lead member of the joint venture may assign its interest to the other partners to the joint venture on the consent of the Employer, such consent not to be unreasonably withheld. (e) Where the Contractor is an SPV, no member of the SPV shall assign its holding in the SPV until the second anniversary of the date of the Commissioning Certificate. Following the second anniversary of the issue of the Commissioning Certificate a member of the SPV on the consent of the Employer, such consent not to be unreasonably withheld, dilute its shareholding in the SPV to the percentage stated in the PDS. |
| Sub-Clause 1.9 |  | Care and Supply of Documents “of a technical nature” is deleted from the last paragraph. |
| Sub-Clause 1 .13 |  | Confidential Details Sub-Clause 1.13 is replaced with the following in its entirety: “1.13 Confidential Details The Contractor’s Personnel and the Employer’s Personnel shall disclose all such confidential and other information as may be reasonably required in order to verify compliance with the Contract and allow its proper implementation. Each of them shall treat the details of the Contract as private and confidential, except to the extent necessary to carry out their respective obligations under the Contract, to comply with applicable Laws or the information is required by the Bank. Each of them shall not publish or disclose any particulars of the Works prepared by the other Party without the previous agreement of the other Party. However, the Contractor shall be permitted to disclose any publicly available information, or information otherwise required to establish his qualifications to compete for other projects.” |
| Sub-Clause 1.14 |  | Compliance with Laws At the end of (b), “failure to do so.” is replaced with “failure to do so, unless the Contractor is impeded to accomplish these actions and shows evidence of its diligence.” |
| Sub-Clause 1.15.2 |  | Joint and Several Liability Before “If the Contractor constitutes” “1.15.1” is added. The following is then added: “1.15.2 If the Contractor is an SPV, throughout the Contract Period, the Contractor shall be bound to maintain its share capital at a minimum level of set out in the Contract Data of the total paid up share capital of the Contractor. The share capital may be increased without the Employer’s prior approval but a written notice of information shall be sent to the Employer. Any reduction of the Contractor’s share capital shall be subject to the prior written consent of the Employer. ##### 1.15.3 The Lead Member who holds at least fifty-one percent (51%) of the subscribed and paid up equity of the Contractor at the Commencement Date shall continue holding at least fifty-one percent (51%) of the subscribed and paid up equity of the Contractor for a period up to the second anniversary of the date of the Commissioning Certificate, [and at least twenty-six percent (26%) for the following five (5) years] subject to the transferee having similar experience to the Lead Member and the approval of the Employer. 1.15.4 The other Members who hold less than forty-nine percent (49%) of the subscribed and paid up equity of the Contractor at the Commencement Date shall continue holding the same percentage of the subscribed and paid up equity of the Concessionaire up to the second anniversary of the date of the Commissioning Certificate.” |
| Sub-Clause 1.16 |  | Inspections and Audit by the Bank The following Sub-Clause is added after Sub-Clause 1.15: “1.16 Inspections and Audit by the Bank Pursuant to paragraph 2.2 e. of Particular Conditions - Part C- Fraud and Corruption, the Contractor shall permit and shall cause its agents (where declared or not), subcontractors, subconsultants, service providers, suppliers, and personnel, to permit, the Bank and/or persons appointed by the Bank to inspect the site and/or the accounts, records and other documents relating to the procurement process, selection and/or contract execution, and to have such accounts, records and other documents audited by auditors appointed by the Bank. The Contractor’s and its Subcontractors’ and subconsultants’ attention is drawn to Sub-Clause 15.8 (Fraud and Corruption) which provides, inter alia, that acts intended to materially impede the exercise of the Bank’s inspection and audit rights constitute a prohibited practice subject to contract termination (as well as to a determination of ineligibility pursuant to the Bank’s prevailing sanctions procedures).” |
| Sub-Clause 2.4 |  | Employer’s Financial Arrangements The Sub-Clause is replaced with the following: “2.4 Employer’s Financial Arrangements The Employer shall submit, before the Commencement Date and thereafter within 28 days after receiving any request from the Contractor, reasonable evidence that financial arrangements have been made and are being maintained which will enable the Employer to pay the Contract Price punctually (as estimated at that time) in accordance with Clause 14 [Contract Price and Payment]. Before the Employer makes any material change to his financial arrangements, the Employer shall give notice to the Contractor with detailed particulars. In addition, if the Bank has notified to the Borrower that the Bank has suspended disbursements under its loan, which finances in whole or in part the execution of the Works, the Employer shall give Notice of such suspension to the Contractor with detailed particulars, including the date of such notification, with a copy to the Employer’s Representative, within 7 days of the Borrower having received the suspension notification from the Bank. If alternative funds will be available in appropriate currencies to the Employer to continue making payments to the Contractor beyond a date 60 days after the date of Bank notification of the suspension, the Employer shall provide reasonable evidence in his Notice of the extent to which such funds will be available.” |
| Sub-Clause 3.1 |  | Employer’s Representative’s Duties and Authority “3.1 Employer’s Representative’s Duties and Authority” the following shall be added to the end of the third paragraph: “The Employer shall promptly inform the Contractor of any change to the authority attributed to the Employer’s Representative.” Paragraph 3.1(c) is followed by: “and (d) any act by the Employer’s Representative in response to a Contractor’s request except as otherwise expressly specified shall be notified in writing to the Contractor within 28 days of receipt.” The following provisions apply thereafter: “The Employer’s Representative shall obtain the specific approval of the Employer before taking action under the-following Sub-Clauses of these Conditions: (a) Sub-Clause 4.12: agreeing or determining an extension of time and/or additional cost. (b) Sub-Clause 13.1: instructing a Variation, except; (i) in an emergency situation as determined by the Employer’s Representative, or (ii) if such a Variation would increase the Accepted Contract Amount by less than the percentage specified in the Contract Data. (c) Sub-Clause 13.3: Approving a proposal for Variation submitted by the Contractor in accordance with Sub Clause 13.1 or 13.2. (d) Sub-Clause 13.4: Specifying the amount payable in each of the applicable currencies Notwithstanding the obligation, as set out above, to obtain approval, if, in the opinion of the Employer’s Representative, an emergency occurs affecting the safety of life or of the Works or of adjoining property, he may, without relieving the Contractor of any of his duties and responsibility under the Contract, instruct the Contractor to execute all such work or to do all such things as may, in the opinion of the Employer’s Representative, be necessary to abate or reduce the risk. The Contractor shall forthwith comply, despite the absence of approval of the Employer, with any such instruction of the Employer’s Representative. The Employer’s Representative shall determine an addition to the Contract Price, in respect of such instruction, and an adjustment to the Time for Completion of Design-Build if any, in accordance with Clause 13 and shall notify the Contractor accordingly, with a copy to the Employer.” |
| Sub-Clause 3.3 |  | Instructions of the Employer’s Representative The last sentence in the second paragraph starting: “These instructions shall be given in writing.” is replaced with: “Whenever practicable, their instructions shall be given in writing. If the Employer’s Representative or a delegated assistant: - gives an oral instruction, - receives a written confirmation of the instruction, from (or on behalf of) the Contractor, within two working days after giving the instruction, and - does not reply by issuing a written rejection and/or instruction within two working days after receiving the confirmation, then the confirmation shall constitute the written instruction of the Employer’s Representative or delegated assistant (as the case may be).” |
| Sub- Clause 3.4 |  | Replacement of the Employer’s Representative Replace the sub-clause with the following: “3.4 Replacement of the Employer’s Representative If the Employer intends to replace the Employer’s Representative, the Employer shall, not less than 21 days before the intended date of replacement, give notice to the Contractor of the name, address and relevant experience of the intended replacement Employer’s Representative. If the Contractor considers the intended replacement Employer’s representative to be unsuitable, he has the right to raise objection against him by notice to the Employer, with supporting particulars, and the Employer shall give full and fair consideration to this objection.” |
| Sub- Clause 3.5 |  | Determinations In the second paragraph replace the first sentence with: “The Employer’s Representative shall give notice to both Parties of each agreement or determination, with supporting particulars, within 28 days from the receipt of the corresponding claim or request except when otherwise specified.” |
| Sub-Clause 4.1 |  | Contractor’s General Obligations At the end of the second paragraph, the following is added: “All equipment, material, and services to be incorporated in or required for the Works shall have their origin in any eligible source country as defined by the Bank.” The following is inserted after the paragraph “The Contractor shall, whenever required by the…”. “The Contractor shall not carry out works, including mobilization and/or pre-construction activities (e.g. clearance for haul roads, site accesses and work site establishment, geotechnical investigations or investigations to select ancillary features such as quarries and borrow pits), unless the Employer’s Representative gives consent, a consent that shall not be unreasonably delayed, to the measures the Contractor proposes to manage the environmental and social risks and impacts, which at a minimum shall include applicable Management Strategies and Implementation Plans (MSIPs) and applying the Code of Conduct for Contractor’s Personnel submitted as part of the Proposal and agreed as part of the Contract. The Contractor shall submit, to the Employer’s Representative for its approval, any additional MSIPs as are necessary to manage the ES risks and impacts of ongoing Works (e.g. excavation, earth works, bridge and structure works, stream and road diversions, quarrying or extraction of materials, concrete batching and asphalt manufacture). These MSIPs collectively comprise the Contractor’s Environmental and Social Management Plan (C-ESMP). The C-ESMP shall be part of the Contractor’s Documents. The Contractor shall review the C-ESMP, periodically (but not less than every six (6) months), and update it as required to ensure that it contains measures appropriate to the Works. The updated C-ESMP shall be submitted to the Employer’s Representative for its approval. The following is added at the end of the Sub-Clause: “The Contractor shall provide relevant contract- related information, as the Employer and/or Employer’s Representative may reasonably request to conduct Stakeholder engagements. “Stakeholder” refers to individuals or groups who: - are affected or likely to be affected by the Contract; and - may have an interest in the Contract. The Contractor shall also directly participate in Stakeholder engagements, as the Employer and/or Employer’s Representative may reasonably request.” |
| Sub-Clause 4.2 |  | Performance security Add in the first paragraph second line after “of the Contract” “and if applicable, an Environmental and Social (ES) Performance Security for compliance with the contractor’s ES obligations”. Delete the third paragraph and replace with the following: “The Contractor shall deliver the Performance Security and, if applicable, an ES Performance Security, to the Employer within 28 days after receiving the Letter of Acceptance and shall send a copy to the Employer’s Representative. The Performance Security and, if applicable, ES Performance Security, shall be issued by a reputable bank or financial institution selected by the Contractor, and shall be in the form annexed to the Particular Conditions, as stipulated by the Employer in the Contract Data, or in another form approved by the Employer.” In the fourth, sixth [and seventh] paragraphs, references to “Performance Security” shall include references to “ES Performance Security” if applicable. Delete the fifth paragraph and replace with: “The Employer shall not make a claim under the Performance Security or the ES Performance Security, as applicable, except for amounts to which the Employer is entitled under the Contract.” At the end of the sub-clause, add “Without limitation to the provisions of the rest of this Sub-Clause, whenever the Employer’s Representative determines an addition or a reduction to the Contract Price as a result of a change in cost and/or legislation, or as a result of a Variation, amounting to more than 25 percent of the portion of the Contract Price payable in a specific currency, the Contractor shall at the Employer’s Representative 's request promptly increase, or may decrease, as the case may be, the value of the Performance Security in that currency by an equal percentage.” At the end of this Sub Clause 4.2, add: “If specified in the Contract Data the Contractor shall obtain at his cost an Environmental and Social (ES) Performance Security for compliance with the Contractor’s ES obligations during the Design-Build Period in the amounts and currencies set out in the Contract Data. The Contractor shall deliver the ES Performance Security to the Employer within 28 days after receiving the Letter of Acceptance and shall send a copy to the Employer's Representative. The ES Performance Security shall be issued by an entity and from within a country (or other jurisdiction) approved by the Employer and shall be in the form annexed to the Particular Conditions, as stipulated by the Employer in the Contract Data, or in another form approved by the Employer. The Contractor shall ensure that the ES Performance Security is valid and enforceable until the issue of the Commissioning Certificate. If the terms of the Performance Security specify its expiry date, and the Contractor has not become entitled to receive the Commissioning Certificate by the date 28 days prior to the expiry date, the Contractor shall extend the validity of the ES Performance Security until the Contractor has been entitled to receive the Commissioning Certificate. Failure by the Contractor to maintain the validity of the ES Performance Security shall be grounds for termination in accordance with Sub-Clause 15.2 [Termination for Contractor's Default]. The Employer shall not make a claim under the ES Performance Security, as applicable, except for amounts to which the Employer is entitled under the Contract. The Employer shall indemnify and hold the Contractor harmless against and from all damages, losses and expenses (including legal fees and expenses) resulting from a claim under the Performance Security which the Employer was not entitled to make. The Employer shall return the ES Performance Security to the Contractor within 21 days after receiving a copy of the Contract Commissioning Certificate. In the following General Conditions sub-clauses references to “Performance Security” shall include references to “ES Performance Security, as applicable”: 2.1- Right of Access to the Site 14.7- Issue of Interim Payment Certificate 14.8(a)- Payment 14.14- Discharge 15.2(a)- Termination 15.5- Employer’s Entitlement to Termination 16.4(a)- Payment on termination”. |
| Sub-Clause 4.3 |  | Contractor’s Representative The following sentence is added at the end of the Sub-Clause: “If the Contractor’s Representative’s delegates are not fluent in the said language, the Contractor shall make competent interpreters available during all working hours in a number deemed sufficient by the Employer’s Representative.” |
| Sub-Clause 4.4 |  | Subcontractors The following is added before “The Contractor shall be responsible for the acts or…” “The Contractor shall require that its Subcontractors execute the Works in accordance with the Contract, including complying with the relevant ES requirements and the obligations set out in Sub-Clause 4.29.” The following is added at the end of the last paragraph of Sub-Clause 4.4: “All subcontracts relating to the Works shall include provisions which entitle the Employer to require the subcontract to be assigned to the Employer under Sub-Clause 15.2. [Termination for Contractor’s Default]. Where practicable, the Contractor shall give fair and reasonable opportunity for contractors from the Country to be appointed as Subcontractors.” |
| Sub-Clause 4.6 |  | Co-operation The following is added as the second paragraph: “The Contractor shall also, as stated in the Employer’s Requirements or as instructed by the Employer’s Representative, cooperate with and allow appropriate opportunities for the Employer’s Personnel to conduct any environmental and social assessment.” in the second paragraph (now third paragraph): “to suffer delays and/or” is added before “to incur Unforeseeable Cost.” |
| Sub-Clause 4.8 |  | The Sub-Clause is replaced with the following: “Health and Safety Obligations The contractor shall: - comply with all applicable health and safety regulations and Laws; - comply with all applicable health and safety obligations specified in the Contract; - take care for the health and safety of all persons entitled to be on the Site and other places, if any, where the Works are being executed; - keep the Site and Works clear of unnecessary obstruction so as to avoid danger to these persons; - provide fencing, lighting, safe access, guarding and watching of the Works until the issue of the Contract Completion Certificate; - provide any Temporary Works (including roadways, footways, guards and fences) which may be necessary, because of the execution of the Works, for the use and protection of the public and of owners and occupiers of adjacent land; - provide health and safety training of Contractor’s Personnel as appropriate and maintain training records; - actively engage the Contractor’s Personnel in promoting understanding, and methods for, implementation of health and safety requirements, as well as in providing information to Contractor’s Personnel, and provision of personal protective equipment without expense to the Contractor’s Personnel; - put in place workplace processes for Contractor’s Personnel to report work situations that they believe are not safe or healthy, and to remove themselves from a work situation which they have reasonable justification to believe presents an imminent and serious danger to their life or health; - Contractor’s Personnel who remove themselves from such work situations shall not be required to return to work until necessary remedial action to correct the situation has been taken. Contractor’s Personnel shall not be retaliated against or otherwise subject to reprisal or negative action for such reporting or removal; - subject to Sub-Clause 4.6, collaborate with the entities and Personnel under paragraph (a), (b) and (c) of Sub-Clause 4.6, in applying the health and safety requirements. This is without prejudice to the responsibility of the relevant entities for the health and safety of their own personnel; and - establish and implement a system for regular (not less than six-monthly) review of health and safety performance and the working environment. Subject to Sub-Clause 4.1, the Contractor shall submit to the Employer’s Representative for its approval a health and safety manual which has been specifically prepared for the Works, the Site and other places (if any) where the Contractor intends to execute the Works. The procedures for review of the health and safety manual and its updates shall be as described in Sub-Clause 5.2 [ Contractor’s Documents]. The health and safety manual shall set out all the health and safety requirements under the Contract, - which shall include at a minimum: - the procedures to establish and maintain a safe working environment without risk to health at all workplaces, machinery, equipment and processes under the control of the Contractor, including control measures for chemical, physical and biological substances and agents; - details of the training to be provided, records to be kept; - the procedures for prevention, preparedness and response activities to be implemented in the case of an emergency event (i.e. an unanticipated incident, arising from both natural and man-made hazards, typically in the form of fire, explosions, leaks or spills, which may occur for a variety of different reasons including failure to implement operating procedures that are designed to prevent their occurrence, extreme weather or lack of early warning); - the measures to be taken to avoid or minimize the potential for community exposure to water-borne, water-based, water-related, and vector-borne diseases, - the measures to be implemented to avoid or minimize the spread of communicable diseases (including transfer of Sexually Transmitted Diseases or Infections (STDs), such as HIV virus) and non-communicable diseases associated with the execution of the Works, taking into consideration differentiated exposure to and higher sensitivity of vulnerable groups. This includes taking measures to avoid or minimize the transmission of communicable diseases that may be associated with the influx of temporary or permanent Contract-related labour; - the policies and procedures on the management and quality of accommodation and welfare facilities if such accommodation and welfare facilities are provided by the Contractor in accordance with Sub-Clause 6.6; and - any other requirements stated in the Employer’s Requirements. - The paragraph starting with: “In addition to the reporting requirement of…” is deleted and replaced with the addition to GC Sub-Clause 4.21 in Sub-Clause 4.21 of the Special Provisions. |
| Sub-Clause 4.12 |  | Unforeseeable Physical Conditions The last paragraph is replaced with: “The Employer’s Representative shall take account of any evidence of the physical conditions foreseen by the Contractor when submitting the Tender, which shall be made available by the Contractor, but shall not be bound by the Contractor’s interpretation of any such evidence.” |
| Sub-Clause 4.13 |  | Rights of Way and Facilities The sub-clause is replaced with the following: “Unless otherwise specified in the Contract the Employer shall provide effective access to and possession of the Site including special and/or temporary rights-of-way which are necessary for the Works. The Contractor shall obtain, at his risk and cost, any additional rights of way or facilities outside the Site which he may require for the purposes of the Works.” |
| Sub-Clause 4.15 |  | Access Route “at Base Date” is added at the end of the first sentence. The following is added at the end of Sub-Clause 4.15: “The Contractor shall take all necessary safety measures to avoid the occurrence of incidents and injuries to any third party associated with the use, if any, of Contractor’s Equipment on public roads or other public infrastructure. The Contractor shall monitor and use road safety incidents and accidents reports to identify negative safety issues, and establish and implement necessary measures to resolve them.” |
| Sub-Clause 4.18 |  | Protection of the Environment ### Sub-Clause 4.18 Protection of the Environment is replaced with: “The Contractor shall take all necessary measures to: - protect the environment (both on and off the Site); and - limit damage and nuisance to people and property resulting from pollution, noise and other results of the Contractor’s operations and/ or activities. The Contractor shall ensure that emissions, surface discharges, effluent and any other pollutants from the Contractor’s activities shall exceed neither the values indicated in the Employer’s Requirements, nor those prescribed by applicable Laws. In the event of damage to the environment, property and/or nuisance to people, on or off Site as a result of the Contractor’s operations, the Contractor shall agree with the Employer’s Representative the appropriate actions and time scale to remedy, as practicable, the damaged environment to its former condition. The Contractor shall implement such remedies at its cost to the satisfaction of the Employer’s Representative.” |
| Sub-Clause 4.21 |  | Progress Reports Sub-Clause 4.21 (g) is replaced by the following: “4.21 (g) the Environmental and Social (ES) metrics set out Particular Conditions- Part D;” The following is added at the end of the Sub-Clause: “In addition to the reporting requirement of this sub-paragraph (g) of Sub-Clause 4.21 [Progress Reports] the Contractor shall inform the Engineer immediately of any allegation, incident or accident, which has or is likely to have a significant adverse effect on the environment, the affected communities, the public, Employer’s Personnel or Contractor’s Personnel. This includes, but is not limited to, any incident or accident causing fatality or serious injury; significant adverse effects or damage to private property; or any allegation of SEA and/or SH. In case of SEA and/or SH, while maintaining confidentiality as appropriate, the type of allegation (sexual exploitation, sexual abuse or sexual harassment), gender and age of the person who experienced the alleged incident should be included in the information. The Contractor, upon becoming aware of the allegation, incident or accident, shall also immediately inform the Engineer of any such incident or accident on the Subcontractors’ or suppliers’ premises relating to the Works which has or is likely to have a significant adverse effect on the environment, the affected communities, the public, Employer’s Personnel or Contractor’s, its Subcontractors’ and suppliers’ personnel. The notification shall provide sufficient detail regarding such incidents or accidents. The Contractor shall provide full details of such incidents or accidents to the Engineer within the timeframe agreed with the Engineer. The Contractor shall require its Subcontractors and suppliers (other than Subcontractors) to immediately notify the Contractor of any incidents or accidents referred to in this Subclause.” |
| Sub-Clause 4.22 |  | Security of the Site The Sub-Clause is replaced with the following: “The Contractor shall be responsible for the security of the Site, and: - for keeping unauthorised persons off the Site; - authorised persons shall be limited to the Contractor’s Personnel, the Employer’s Personnel, and to any other personnel identified as authorised personnel (including the Employer’s other contractors on the Site), by a Notice from the Employer or the Employer’s Representative to the Contractor. Subject to Sub-Clause 4.1, the Contractor shall submit for the Employer’s Representative’s No-objection a security management plan that sets out the security arrangements for the Site. The Contractor shall (i) conduct appropriate background checks on any personnel retained to provide security; (ii) train the security personnel adequately (or determine that they are properly trained) in the use of force (and where applicable, firearms), and appropriate conduct towards Contractor’s Personnel, Employer’s Personnel and affected communities; and (iii) require the security personnel to act within the applicable Laws and any requirements set out in the Employer’s Requirements. The Contractor shall not permit any use of force by security personnel in providing security except when used for preventive and defensive purposes in proportion to the nature and extent of the threat. In making security arrangements, the Contractor shall also comply with any additional requirements stated in the Employer’s Requirements.” |
| Sub-Clause 4.24 |  | The heading is replaced with: “Archaeological and Geological Findings”. The first paragraph is replaced with the following: “All fossils, coins, articles of value or antiquity, structures, groups of structures, and other remains or items of geological, archaeological, paleontological, historical, architectural or religious interest found on the Site shall be placed under the care and custody of the Employer. The Contractor shall: - take all reasonable precautions, including fencing-off the area or site of the finding, to avoid further disturbance and prevent Contractor’s Personnel or other persons from removing or damaging any of these findings; - train relevant Contractor’s Personnel on appropriate actions to be taken in the event of such findings; and - implement any other action consistent with the requirements of the Employer’s Requirements and relevant Laws.” |
| Sub-Clause 4.26 |  | Demolition: the following Sub-Clause is added: “The Contractor shall not demolish any building or structure except where specified in the Employer’s Requirements, or with the prior written approval of the Employer’s Representative. The conditions for the re-use, sale and disposal of demolished materials shall be as specified in the Employer Requirements.” |
| Sub-clause 4.27 |  | Existing Facilities: the following Sub-Clause is added: “The Contractor shall take over, rehabilitate, upgrade, operate and maintain the Existing Facilities to the extent specified in the Employer’s Requirements. Unless stated otherwise in the Employer’s Requirements, the Contractor shall provide, and pay for, all labour, equipment, materials (including spare parts and consumables), and electricity necessary to operate and maintain the Existing Facilities. During the Design-Build Period, (a) the Contractor shall use all reasonable endeavors to meet the standards of performance specified for the Existing Facilities in the Employer’s Requirements; (b) The Employer shall indemnify and hold harmless the Contractor against any and all claims made against it in respect of the operation of the Existing Facilities to the extent that the condition or design of the Existing Facilities renders them unable to meet the applicable performance standards.” As at the date of commencement of the Operation Service the Existing Facility, unless specified otherwise in the Employer’s Requirements, will be deemed to form part of the Works, and all references in the Contract to Works, Permanent Works, Plant and Site etc. shall be deemed to include the Existing Facilities. |
| Sub-clause 4.28 Suppliers (other than Subcontractors) |  | The following Sub-Clauses are added: 4.28.1 Forced Labour The Contractor shall take measures to require its suppliers (other than Subcontractors) not to employ or engage forced labour including trafficked persons as described in Sub-Clause 6.20. If forced labour/trafficking cases are identified, the Contractor shall take measures to require the suppliers to take appropriate steps to remedy them. Where the supplier does not remedy the situation, the Contractor shall within a reasonable period substitute the supplier with a supplier that is able to manage such risks. 4.28.2 Child labour The Contractor shall take measures to require its suppliers (other than Subcontractors) not to employ or engage child labour as described in Sub-Clause 6.21. If child labour cases are identified, the Contractor shall take measures to require the suppliers to take appropriate steps to remedy them. Where the supplier does not remedy the situation, the Contractor shall within a reasonable period substitute the supplier with a supplier that is able to manage such risks. 4.28.3 Serious Safety Issues The Contractor, including its Subcontractors, shall comply with all applicable safety obligations, including as stated in Sub-Clauses 4.4, 4.8 and 6.7. The Contractor shall also take measures to require its suppliers (other than Subcontractors) to adopt procedures and mitigation measures adequate to address safety issues related to their personnel. If serious safety issues are identified, the Contractor shall take measures to require the suppliers to take appropriate steps to remedy them. Where the supplier does not remedy the situation, the Contractor shall within a reasonable period substitute the supplier with a supplier that is able to manage such risks. 4.28.4 Obtaining natural resource materials in relation to supplier The Contractor shall obtain natural resource materials from suppliers that can demonstrate, through compliance with the applicable verification and/ or certification requirements, that obtaining such materials is not contributing to the risk of significant conversion or significant degradation of natural or critical habitats such as unsustainably harvested wood products, gravel or sand extraction from river beds or beaches. If a supplier cannot continue to demonstrate that obtaining such materials is not contributing to the risk of significant conversion or significant degradation of natural or critical habitats, the Contractor shall within a reasonable period substitute the supplier with a supplier that is able to demonstrate that they are not significantly adversely impacting the habitats. |
| Sub-clause 4.29 |  | The following Sub-Clause is added: “Code of Conduct The Contractor shall have a Code of Conduct for the Contractor’s Personnel. The Contractor shall take all necessary measures to ensure that each Contractor’s Personnel is made aware of the Code of Conduct including specific behaviors that are prohibited, and understands the consequences of engaging in such prohibited behaviors. These measures include providing instructions and documentation that can be understood by the Contractor’s Personnel and seeking to obtain that person’s signature acknowledging receipt of such instructions and/or documentation, as appropriate. The Contractor shall also ensure that the Code of Conduct is visibly displayed in multiple locations on the Site and any other place where the Works will be carried out, as well as in areas outside the Site accessible to the local community and project affected people. The posted Code of Conduct shall be provided in languages comprehensible to Contractor’s Personnel, Employer’s Personnel and the local community. The Contractor’s Management Strategy and Implementation Plans shall include appropriate processes for the Contractor to verify compliance with these obligations.” |
| Sub-Clause 6.1 |  | Engagement of Staff and Labour The following paragraphs are added at the end of the Sub-Clause: “The Contractor shall provide the Contractor’s Personnel information and documentation that are clear and understandable regarding their terms and conditions of employment. The information and documentation shall set out their rights under relevant labour Laws applicable to the Contractor’s Personnel (which will include any applicable collective agreements), including their rights related to hours of work, wages, overtime, compensation and benefits, as well as those arising from any requirements in the Employer’s Requirements. The Contractor’s Personnel shall be informed when any material changes to their terms or conditions of employment occur. The Contractor is encouraged, to the extent practicable and reasonable, to employ staff and labour with appropriate qualifications and experience from sources within the Country.” |
| Sub-Clause 6.2 |  | Rates of Wages and Conditions of Labour The following paragraphs are added at the end of the Sub-Clause: “The Contractor shall inform the Contractor’s Personnel about: - any deduction to their payment and the conditions of such deductions in accordance with the applicable Laws or as stated in the Employer’s Requirements; and - their liability to pay personal income taxes in the Country in respect of such of their salaries, wages, allowances and any benefits as are subject to tax under the Laws of the Country for the time being in force. The Contractor shall perform such duties in regard to such deductions thereof as may be imposed on him by such Laws. Where required by applicable Laws or as stated in the Employer’s Requirements, the Contractor shall provide the Contractor’s Personnel written notice of termination of employment and details of severance payments in a timely manner. The Contractor shall have paid the Contractor’s Personnel (either directly or where appropriate for their benefit) all due wages and entitlements including, as applicable, social security benefits and pension contributions, on or before the end of their engagement/ employment.” |
| Sub-Clause 6.5 |  | Working Hours The following is inserted at the end of the Sub-Clause: “The Contractor shall provide the Contractor’s Personnel annual holiday and sick, maternity and family leave, as required by applicable Laws or as stated in the Employer’s Requirements.” |
| Sub-Clause 6.6 |  | Facilities for Staff and Labour The following is added as the last paragraph: “If stated in the Employer’s Requirements, the Contractor shall give access to or provide services that accommodate the physical, social and cultural needs of the Contractor’s Personnel. The Contractor shall also provide similar facilities for the Employer’s Personnel as stated in the Employer’s Requirements.” |
| Sub-Clause 6.7 |  | Health and Safety In the beginning of the Sub-Clause: “The Contractor shall” is replaced with: In addition to the requirements of Sub-Clause 4.8 [Health and Safety Obligations], the Contractor shall” The first sentence of the last paragraph is deleted. |
| Sub-Clause 6.9 |  | Contractor’s personnel The Sub-Clause is replaced with: ““The Contractor’s Personnel (including Key Personnel, if any) shall be appropriately qualified, skilled, experienced and competent in their respective trades or occupations. The Employer’s Representative may require the Contractor to remove (or cause to be removed) any person employed on the Site or Works, including the Contractor’s Representative and Key Personnel (if any), who: - persists in any misconduct or lack of care; - carries out duties incompetently or negligently; - fails to comply with any provision of the Contract; - persists in any conduct which is prejudicial to safety, health, or the protection of the environment; - based on reasonable evidence, is determined to have engaged in Fraud and Corruption during the execution of the Works; - has been recruited from the Employer’s Personnel in breach of Sub-Clause 6.3 [Persons in the Service of the Employer]; - undertakes behaviour which breaches the Code of Conduct for Contractor’s Personnel (ES). If appropriate, the Contractor shall then promptly appoint (or cause to be appointed) a suitable replacement with equivalent skills and experience. Notwithstanding any requirement from the Employer’s Representative to remove or cause to remove any person, the Contractor shall take immediate action as appropriate in response to any violation of (a) through (g) above. Such immediate action shall include removing (or causing to be removed) from the Site or other places where the Works are being carried out, any Contractor’s Personnel who engages in (a), (b), (c), (d), (e) or (g) above or has been recruited as stated in (f) above. In the case of replacement of the Contractor’s Representative, Sub-Clause 4.3 [Contractor’s Representative] shall apply. In the case of replacement of Key Personnel (if any), the replacement provision in this Sub-Clause 6.9 shall apply. If the Contractor intends to replace a Key Personnel, the Contractor shall, not less than 30 days before the intended date of replacement, give notice to the Employer’s Representative, the name, address, academic qualifications and relevant experience of the intended replacement Key Personnel. The Contractor shall not, without the prior consent of the Employer’s Representative, revoke the appointment of the Key Personnel or appoint a replacement.” |
| The following Sub-Clauses 6.12 to 6.25 are added after sub-clause 6.11 |  |  |
| ### Sub-Clause 6.12 Foreign Personnel |  | The Contractor may bring in to the Country any foreign personnel who are necessary for the execution of the Works to the extent allowed by the applicable Laws. The Contractor shall ensure that these personnel are provided with the required residence visas and work permits. The Employer will, if requested by the Contractor, use its best endeavours in a timely and expeditious manner to assist the Contractor in obtaining any local, state, national, or government permission required for bringing in the Contractor’s personnel. The Contractor shall be responsible for the return of these personnel to the place where they were recruited or to their domicile. In the event of the death in the Country of any of these personnel or members of their families, the Contractor shall similarly be responsible for making the appropriate arrangements for their return or burial. |
| ### Sub-Clause 6.13 Supply of Foodstuffs |  | The Contractor shall arrange for the provision of a sufficient supply of suitable food as may be stated in the Employer’s Requirements at reasonable prices for the Contractor’s Personnel for the purposes of or in connection with the Contract. |
| ### Sub-Clause 6.14 Supply of Water |  | The Contractor shall, having regard to local conditions, provide on the Site an adequate supply of drinking and other water for the use of the Contractor’s Personnel. |
| ### Sub-Clause 6.15 Measures against Insect and Pest Nuisance |  | The Contractor shall at all times take the necessary precautions to protect the Contractor’s Personnel employed on the Site from insect and pest nuisance, and to reduce the danger to their health. The Contractor shall comply with all the regulations of the local health authorities, including use of appropriate insecticide. |
| ### Sub-Clause 6.16 Alcoholic Liquor or Drugs |  | The Contractor shall not, otherwise than in accordance with the Laws of the Country, import, sell, give, barter or otherwise dispose of any alcoholic liquor or drugs, or permit or allow importation, sale, gift, barter or disposal thereto by Contractor’s Personnel. |
| ### Sub-Clause 6.17 Arms and Ammunition |  | The Contractor shall not give, barter, or otherwise dispose of, to any person, any arms or ammunition of any kind, or allow Contractor’s Personnel to do so. |
| ### Sub-Clause 6.18 Festivals and Religious Customs |  | The Contractor shall respect the Country’s recognized festivals, days of rest and religious or other customs. |
| ### Sub-Clause 6.19 Funeral Arrangements |  | The Contractor shall be responsible, to the extent required by local regulations, for making any funeral arrangements for any of its local employees who may die while engaged upon the Works. |
| ### Sub-Clause 6.20 Forced Labour |  | The Contractor, including its Subcontractors, shall not employ or engage forced labour. Forced labour consists of any work or service, not voluntarily performed, that is exacted from an individual under threat of force or penalty, and includes any kind of involuntary or compulsory labour, such as indentured labour, bonded labour or similar labour-contracting arrangements. No persons shall be employed or engaged who have been subject to trafficking. Trafficking in persons is defined as the recruitment, transportation, transfer, harbouring or receipt of persons by means of the threat or use of force or other forms of coercion, abduction, fraud, deception, abuse of power, or of a position of vulnerability, or of the giving or receiving of payments or benefits to achieve the consent of a person having control over another person, for the purposes of exploitation. |
| ### Sub-Clause 6.21 Child Labour |  | The Contractor, including its Subcontractors, shall not employ or engage a child under the age of 14 unless the national law specifies a higher age (the minimum age). The Contractor, including its Subcontractors, shall not employ a child between the minimum age and the age of 18 in a manner that is likely to be hazardous, or to interfere with, the child’s education, or to be harmful to the child’s health or physical, mental, spiritual, moral, or social development. The Contractor including its Subcontractors, shall only employ children between the minimum age and the age of 18 after an appropriate risk assessment has been conducted by the Contractor with the Employer’s Representative’s consent. The Contractor shall be subject to regular monitoring by the Employer’s Representative that includes monitoring of health, working conditions and hours of work. Work considered hazardous for children is work that, by its nature or the circumstances in which it is carried out, is likely to jeopardize the health, safety, or morals of children. Such work activities prohibited for children include work: - with exposure to physical, psychological or sexual abuse; - underground, underwater, working at heights or in confined spaces; - with dangerous machinery, equipment or tools, or involving handling or transport of heavy loads; - in unhealthy environments exposing children to hazardous substances, agents, or processes, or to temperatures, noise or vibration damaging to health; or under difficult conditions such as work for long hours, during the night or in confinement on the premises of the employer. |
| ### Sub-Clause 6.22 Employment Records of Workers |  | The Contractor shall keep complete and accurate records of the employment of labour at the Site. The records shall include the names, ages, genders, hours worked and wages paid to all workers. These records shall be summarised on a monthly basis and submitted to the Employer’s Representative. These records shall be included in the details to be submitted by the Contractor under Sub-Clause 6.10 [Records of Contractor’s Personnel and Equipment]. |
| ### Sub-Clause 6.23 Workers’ Organisations |  | In countries where the relevant labour laws recognise workers’ rights to form and to join workers’ organisations of their choosing and to bargain collectively without interference, the Contractor shall comply with such laws. In such circumstances, the role of legally established workers’ organizations and legitimate workers’ representatives will be respected, and they will be provided with information needed for meaningful negotiation in a timely manner. Where the relevant labour laws substantially restrict workers’ organisations, the Contractor shall enable alternative means for the Contractor’s Personnel to express their grievances and protect their rights regarding working conditions and terms of employment. The Contractor shall not seek to influence or control these alternative means. The Contractor shall not discriminate or retaliate against the Contractor’s Personnel who participate, or seek to participate, in such organisations and collective bargaining or alternative mechanisms. Workers’ organisations are expected to fairly represent the workers in the workforce. |
| ### Sub-Clause 6.24 Non-Discrimination and Equal Opportunity |  | The Contractor shall not make decisions relating to the employment or treatment of Contractor’s Personnel on the basis of personal characteristics unrelated to inherent job requirements. The Contractor shall base the employment of Contractor’s Personnel on the principle of equal opportunity and fair treatment, and shall not discriminate with respect to any aspects of the employment relationship, including recruitment and hiring, compensation (including wages and benefits), working conditions and terms of employment, access to training, job assignment, promotion, termination of employment or retirement, and disciplinary practices. Special measures of protection or assistance to remedy past discrimination or selection for a particular job based on the inherent requirements of the job shall not be deemed discrimination. The Contractor shall provide protection and assistance as necessary to ensure nondiscrimination and equal opportunity, including for specific groups such as women, people with disabilities, migrant workers and children (of working age in accordance with Sub-Clause 6.21). |
| ### Sub-Clause 6.25 ### Contractor’s Personnel Grievance Mechanism |  | The Contractor shall have a grievance mechanism for Contractor’s Personnel, and where relevant the workers’ organizations stated in Sub-Clause 6.23, to raise workplace concerns The grievance mechanism shall be proportionate to the nature, scale, risks and impacts of the Contract. The mechanism shall address concerns promptly, using an understandable and transparent process that provides timely feedback to those concerned in a language they understand, without any retribution, and shall operate in an independent and objective manner. The Contractor’s Personnel shall be informed of the grievance mechanism at the time of engagement for the Contract, and the measures put in place to protect them against any reprisal for its use. Measures will be put in place to make the grievance mechanism easily accessible to all Contractor’s Personnel. The grievance mechanism shall not impede access to other judicial or administrative remedies that might be available, or substitute for grievance mechanisms provided through collective agreements. The grievance mechanism may utilize existing grievance mechanisms, providing that they are properly designed and implemented, address concerns promptly, and are readily accessible to such Contractor’s Personnel. Existing grievance mechanisms may be supplemented as needed with Contract-specific arrangements. |
| ### Sub-Clause 6.26 ### Training of Contractor’s Personnel |  | The Contractor shall provide appropriate training to relevant Contractor’s Personnel on ES aspects of the Contract, including appropriate sensitization on prohibition of SEA and health and safety training referred to in Sub-Clause 4.8 As stated in the Employer’s Requirements or as instructed by the Employer’s Representative, the Contractor shall also allow appropriate opportunities for the relevant Contractor’s Personnel to be trained on ES aspects of the Contract by the Employer’s Personnel. The Contractor shall provide training on SEA, including its prevention, to any of its personnel who has a role to supervise other Contractor’s Personnel. |
| Sub-Clause 7.3 Inspection |  | The following is added in the first paragraph after “Employer’s Personnel” “(including the Bank staff or consultants acting on the Bank’s behalf, stakeholders and third parties, such as independent experts, local communities, or non-governmental organizations)” Sub-Clause 7.3 (c) is replaced with: “carry out other duties and inspections, including carrying out environmental and social audit.” |
| Sub-Clause 7.4 |  | Testing The second paragraph shall start as: “Except as otherwise specified in the Contract, the Contractor shall….”. |
| Sub-Clause 7.7 |  | Ownership of Plant and Materials The first paragraph shall start as: “Except as otherwise specified in the Contract, ….” Further in each of point (b) and (c), “when the Contractor is entitled to payment of the value” is replaced with “when the Contractor is paid the corresponding value”. The following is added at the end of the sub-clause: “For the avoidance of doubt, vehicles, trucks, mobile plant and site equipment (other than temporary mobile plant and temporary site equipment brought onto the site to undertake specific remedial tasks), tools, office equipment, software and office consumables used by the Contractor for the Operation Service shall become the property of the Employer. Vehicles used for personal transportation of the Contractor’s Personnel and computers and mobile devices allocated for the personal use of the Contractor’s Personnel shall be Contractor’s Equipment. The Contractor shall maintain up-to-date inventories of the Contractor’s Equipment, Materials and Temporary Works throughout the term of the Contract.” |
| Sub-Clause 8.1 |  | Commencement of Work The sub- clause is replaced in its entirety with the following: “8.1 Commencement of Work Except as otherwise specified in the Contract, the Commencement Date shall be the date at which the following precedent conditions have all been fulfilled and the Employer’s Representative’s notification recording the agreement of both Parties on such fulfilment and instructing to commence the Work is received by the Contractor: (a) signature of the Contract Agreement by both Parties, and if required, approval of the Contract by relevant authorities of the Country; (b) delivery to the Contractor of reasonable evidence of the Employer’s financial arrangements (under Sub-Clause 2.4 [Employer’s Financial Arrangements]); (c) except if otherwise specified in the Contract Data, effective access to and possession of the Site given to the Contractor together with such permission(s) under (a) of Sub-Clause 1.14 [Compliance with Laws] as required for the commencement of the Works; (d) receipt by the Contractor of the Advance Payment under Sub-Clause 14.2 [Advance Payment] provided that the corresponding bank guarantee has been delivered by the Contractor; and (e) constitution of the DAB in accordance with Sub-Clause 20.3 and Sub-Clause 20.4 as applicable. Subject to Sub-Clause 4.1 on the Management Strategies and Implementation Plans and the C-ESMP and Sub-Clause 4.8 on the health and safety manual, the Contractor, shall commence the execution of the Works as soon as is reasonably practicable after the Commencement Date, and shall then proceed with the Works with due expedition and without delay.” If the said Employer’s Representative’s instruction is not received by the Contractor within 180 days from his receipt of the Letter of Acceptance, the Contractor shall be entitled to terminate the Contract under Sub-Clause 16.2 [Termination by Contractor]. |
| Sub-Clause 9.5 |  | Rate of Progress The following is added as the last paragraph of the sub- clause: “Additional costs of revised methods including acceleration measures, instructed by the Employer’s Representative to reduce delays resulting from causes listed under Sub-Clause 8.4 [Extension of Time for Completion] shall be paid by the Employer, without generating, however, any other additional payment benefit to the Contractor.” |
| Sub-Clause 9.11 |  | Resumption of Work The following is added at the end of the sub-clause after “suspension”: “after receiving from the Employer’s Representative an instruction to this effect under Clause 13 [Variations and Adjustments].” |
| Sub-Clause 10.1 |  | General Requirements: The following is added after Operation Management Requirements: “, and Performance Standards.” Sub-Clause 10.1 General Requirements: The second paragraph is replaced with the following: “The Contractor shall follow the requirements of the operation and maintenance manuals and any additional Operation Service plans and manuals, prepared by the Contractor in accordance with the Operation Management Requirements. No significant alteration to such arrangements and methods shall be made without the prior approval of the Employer's Representative.” |
| Sub-Clause 10.2 |  | Commencement of Operation Service: The first paragraph is replaced with the following: “Unless otherwise stated in the Contract Data, the date of commencement of the Operation Service shall be the date seven days following the date of issuance of the Commissioning Certificate issued under Sub-Clause 11.7 [Commissioning Certificate], or such earlier date the Parties may agree to.” |
| Sub-Clause 10.4 |  | Delivery of Raw Materials In the first paragraph, “Employer’s Requirements” is deleted and replaced with “Contract Data”. |
| Sub-Clause 10.6 |  | Delays and Interruptions during the Operation Service: Sub-paragraph (a) is replaced with the following “(a) If there are any delays or interruptions during the Operation Service which are caused by the Contractor or by a cause for which the Contractor is responsible, the Contractor, subject to Sub-Clause 3.5 [Determinations], shall pay the Employer the performance damages for delay and interruptions specified in the Schedule of Performance Damages. The Employer shall be entitled to recover the amounts due by making corresponding deductions from the payments due to the Contractor. However, the amount of Performance Damages in any contract year of the Operation Service, and the total amount of Performance Damages payable by the Contractor to the Employer, shall not exceed the amounts stated in the Contract Data. There will be no extension of the period of the Operation Service as a result of any such delay or interruption. If a delay or interruption results in a failure to meet Performance Standards and the Contractor is also liable to pay performance damages pursuant to Sub-Clause 10.7, then damages shall not be imposed under both clauses, and the Employer shall determine whether to impose damages under this Sub-Clause 10.6 (a) or under Sub-Clause 10.7.” |
| Sub-Clause 10.7 |  | Failure to Reach Production Outputs: replace title with “Failure to Meet Performance Standards” and replace entire sub-clause with the following: “In the event that the Contractor fails to achieve the Performance Standards required under the Contract, the Parties shall jointly establish the cause of such failure. (a) If the failure is due to the Employer or any of his servants or agents, then, after consultation with the Contractor, the Employer shall give written instruction to the Contractor of the measures which the Employer requires the Contractor to take. If the Contractor suffers any additional cost as a result of the failure or the measures instructed by the Employer, the Employer, subject to Sub-Clause 3.5 [Determinations] and Sub-Clause 20.1 [Contractor's Claims], shall pay the Contractor his Cost Plus Profit. (b) If the failure is due to the Contractor then, after due consultation with the Employer, the Contractor shall at its own expense make any changes, modifications or additions to the Works, to its operating procedures, and to the Contractor’s Personnel, as may be necessary to bring the Works and Operation Service into compliance with the Performance Standards. If the failure relates to a Performance Standard for which damages are specified in the Schedule of Performance Damages, then he Contractor, subject to Sub-Clause 3.5 [Determinations], shall pay the Employer the performance damages specified in the Schedule of Performance Damages. The Employer shall be entitled to recover the amount due by making corresponding deductions from the payments due to the Contractor. The amount of compensation payable by the Contractor to the Employer under this sub-clause in any contract year of the Operation Service Period and total amount of compensation payable by the Contractor under this Sub-Clause 10.7 (Failures to meet Performance Standards) shall not exceed the amounts stated in the Contract Data. Unless otherwise stated in the Contract Data, if the failure continues for a period of more than 84 days and the Contractor is unable to achieve the required Performance Standards, the Employer may either: (i) continue with the Operation Service at a reduced level of compensation determined in accordance with Sub-Clause 3.5 [Determinations]; or, (ii) give Notice to the Contractor of not less than 56 days of its decision to terminate the Contract, in accordance with Sub-Clause 15.2 [Termination for Contractor's Default]. In such an event, the Employer shall be free to continue the Operation Service itself or by others.” |
| Sub-Clause 10.9 |  | Ownership of Output and Revenue: Add at the beginning of the paragraph the following: “Unless specified otherwise in the Contract Data,” |
| Sub-Clause 11.1 |  | In the fifth paragraph, “Schedule of Guarantees” is replaced with “Schedule of Performance Standards” |
| Sub-Clause 11.8 |  | Joint Inspection Prior to Contract Completion: Replace the first paragraph with the following: “Not less than two years prior to the expiry date of the Operation Service Period, the Employer's Representative and the Contractor shall carry out a joint inspection of the Works and, within 28 days of the completion of the joint inspection, the Contractor shall submit a report on the condition of the Works, for the Approval of the Employer’s Representative, identifying all remedial works and asset replacements (excluding routine maintenance works) that are necessary a) to satisfy the handback requirement specified in the Employer’s Requirements, and b) to ensure that the Works can be operated in full compliance with the Performance Standards after the Contract Completion Date.” |
| Sub-Clause 13.1 |  | Right to Vary In the first paragraph, “The variation shall not comprise the omission of any work which is to be carried out by others” is deleted. In the second paragraph, added as (iv): “such Variation triggers a substantial change in the sequence or progress of the Works.” In the second paragraph, “Schedule of Guarantees” is replaced with “Schedule of Performance Standards” |
| Sub-Clause 13.3 |  | Variation procedure The following is added to the end of Sub-Clause 13.3. (a): “and sufficient ES information to enable an evaluation of ES risks and impacts;” |
| Sub-Clause 13.5 |  | Provisional Sums The following is added at the end of the sub-clause: “The Provisional Sum shall be used to cover the Employer's share of the DAB members’ fees and expenses, in accordance with Clause 20.3. No prior instruction of the Employer’s Representative shall be required with respect to the work of the DAB. The Contractor shall submit the DAB members’ invoices and satisfactory evidence of having paid 100% of such invoices as part of the substantiation of those Statements submitted under Sub-Clause 14.3.” |
| Sub-Clause 13.6 | Adjustments for Change in Legislation The following is added at the end of the sub-clause: “Notwithstanding the foregoing, the Contractor shall not be entitled to an extension of time if the relevant delay has already been taken into account in the determination of a previous extension of time and such Cost shall not be separately paid if the same shall already have been taken into account in the indexing of any inputs to the table of adjustment data in accordance with the provisions of Sub-Clause 13.8 [Adjustments for Changes in Cost].” |  |
| Sub-Clause 13.9 | The following Sub-Clause is added “13.9 Adjustments for Changes in Influent Quality: If provided for in the Contract Data, the Contract Price and/or Performance Standards shall be adjusted to take account of the impacts of long term changes in the characteristics of the Influent received at the delivery point to the Works, relative to the Influent Baseline, provided that: - The changes in Influent characteristics are sustained and permanent; - The changes give rise to an increase or decrease in the Contractor’s annual Operation Service costs (excluding any Asset Replacement amounts) of greater than 5 % [or Employer may insert alternative value] relative to what the costs would have been had the long term changes in the characteristics of the Influent not occurred. In such case, either the Employer or the Contractor shall be entitled to initiate an adjustment in the Contract Price and/or Performance Standards. The Contractor shall be entitled to make a claim for an adjustment in the Contract Price in accordance with Sub-Clause 20.1 (Contractor’s Claims), and/or may submit a proposal for an adjustment in the Performance Standards under Sub-Clause 13.2 (Value Engineering). The Employer shall be entitled to vary the Contract Price or Performance Standards by issuing a Variation in accordance with Clause 13 (Variations and Adjustments) Following a successful claim under this Sub-Clause, the Employer’s Representative shall update the Influent Baseline to reflect the long term changes to the characteristics, and the updated Influent Baseline shall be used as the baseline against which to evaluate any further claims for price adjustment under this Sub-Clause.” |  |
| Sub-Clause 14.1 | The Contract Price The following is added at the end of the Sub-Clause: “Notwithstanding the provisions of subparagraph (b), Contractor's Equipment, including essential spare parts therefor, imported by the Contractor for the sole purpose of executing the Contract shall be required to pay import duties and taxes upon importation.” |  |
| Sub-Clause 14.2 | Advance payment The sub-clause is replaced in its entirety by the following: “14.2 Advance Payment The Employer shall make an advance payment, as an interest-free loan for mobilization and cash flow support, when the Contractor submits a guarantee in accordance with this Sub-Clause. The total advance payment, the number and timing of instalments (if more than one), and the applicable currencies and proportions, shall be as stated in the Contract Data. Unless and until the Employer receives this guarantee, or if the total advance payment is not stated in the Contract Data, this Sub-Clause shall not apply. The Employer’s Representative shall deliver to the Employer and to the Contractor an Interim Payment Certificate for the advance payment or its first instalment after receiving a Statement (under Sub-Clause 14.3 [Application for Advance and Interim Payment Certificates]) and after the Employer receives (i) the Performance Security in accordance with Sub-Clause 4.2 [Performance Security] and (ii) a guarantee in amounts and currencies equal to the advance payment. This guarantee shall be issued by a reputable bank or financial institution selected by the Contractor and shall be [based on the sample form included in the tender documents][in the form annexed to the Particular Conditions] or in another form approved by the Employer. The Contractor shall ensure that the guarantee is valid and enforceable until the advance payment has been repaid, but its amount shall be progressively reduced by the amount repaid by the Contractor as indicated in the Payment Certificates. If the terms of the guarantee specify its expiry date, and the advance payment has not been repaid by the date 28 days prior to the expiry date, the Contractor shall extend the validity of the guarantee until the advance payment has been repaid. Unless stated otherwise in the Contract Data, the advance payment shall be repaid through percentage deductions from the interim payments determined by the Employer’s Representative in accordance with Sub-Clause 14.7 [Issue of Advance and Interim Payment Certificates], as follows: - deductions shall commence in the next interim Payment Certificate following that in which the total of all certified interim payments (excluding the advance payment and deductions and repayments of retention) exceeds 30 percent (30%) of the Accepted Contract Amount for the Design Build less Provisional Sums; and - deductions shall be made at the amortization rate stated in the Contract Data of the amount of each Interim Payment Certificate (excluding the advance payment and deductions for its repayments as well as deductions for retention money) in the currencies and proportions of the advance payment until such time as the advance payment has been repaid; provided that the advance payment shall be completely repaid prior to the time when 90 percent (90%) of the Accepted Contract Amount for the Design Build less Provisional Sums has been certified for payment. If the advance payment has not been repaid prior to the issue of the Commissioning Certificate for the Works or prior to termination under Clause 15 [Termination by Employer], Clause 16 [Suspension and Termination by Contractor] or Clause 18 [Exceptional Risks] (as the case may be), the whole of the balance then outstanding shall immediately become due and in case of termination under Clause 15 [Termination by Employer], except for Sub-Clause 15.5 [Employer’s Entitlement to Termination for Employer’s Convenience], payable by the Contractor to the Employer.” |  |
| Sub-Clause 14.3 | Application for Advance and Interim Payment Certificates The following is added to the end of the second paragraph: “The Contractor shall prepare separate Statements for the Design-Build and for the Operation Service.” |  |
| Sub- Clause 14.7 | Issue of Advance and Interim Payment Certificates In the first paragraph, “issue to the Employer” is replaced with “deliver to the Employer and to the Contractor.” The following is added to the third paragraph as (c): - if the Contractor was, or is, failing to perform any ES obligations or work under the Contract, the value of this work or obligation, as determined by the Employer’s Representative, may be withheld until the work or obligation has been performed, and/or the cost of rectification or replacement, as determined by the Employer’s Representative, may be withheld until rectification or replacement has been completed. Failure to perform includes, but is not limited to the following: - failure to comply with any ES requirements described in the Employer’s Requirements; - failure to regularly review C-ESMP and/or update it in a timely manner to address emerging ES issues, or anticipated risks or impacts; - failure to implement the C-ESMP e.g. failure to provide required training or sensitization; - failing to have appropriate consents/permits prior to undertaking Works or related activities; - failure to submit ES report/s (as described in Particular Conditions 4.21), or failure to submit such reports in a timely manner; - failure to implement remediation as instructed by the Employer’s Representative within the specified timeframe (e.g. remediation addressing non-compliance/s). |  |
| Sub-Clause 14.8 | Payment (b) and (c) are replaced with the following “(b) the amount certified in each Interim Payment Certificate within 56 days after the Employer’s Representative receives the Statement and supporting documents; or, at a time when the Bank’s loan or credit (from which part of the payments to the Contractor is being made) is suspended, the amount shown on any statement submitted by the Contractor within 14 days after such statement is submitted, any discrepancy being rectified in the next payment to the Contractor; and (c) the amount certified in the Final Payment Certificate within 56 days after the Employer receives this Payment Certificate; or, at a time when the Bank’s loan or credit (from which part of the payments to the Contractor is being made) is suspended, the undisputed amount shown in the Final Statement within 56 days after the date of notification of the suspension in accordance with Sub-Clause 16.2 [Termination by Contractor].” |  |
| Sub-Clause 14.9 | Delayed Payment In the second paragraph,4th line, after “currency of payment,” the following is inserted: “or, if not available, the interbank offered rate,” |  |
| Sub-Clause 14.10 | Payment of Retention money The following is added to the end of the Sub-Clause: “Unless otherwise stated in the Contract, when the Commissioning Certificate has been issued for the Works and the first half of the Retention Money has been certified for payment by the Employer’s Representative, the Contractor shall be entitled to substitute a guarantee, in the form annexed to the Particular Conditions or in another form approved by the Employer and issued by a reputable bank or financial institution selected by the Contractor, for the second half of the Retention Money. The Contractor shall ensure that the guarantee is in the amounts and currencies of the second half of the Retention Money and is valid and enforceable until the Contractor has executed and completed the Works and remedied any defects, as specified for the Performance Security in Sub-Clause 4.2. On receipt by the Employer of the required guarantee, the Employer’s Representative shall certify and the Employer shall pay the second half of the Retention Money. The release of the second half of the Retention Money against a guarantee shall then be in lieu of the release under the second paragraph of this Sub-Clause. The Employer shall return the guarantee to the Contractor within 21 days after receiving a copy of the performance certificate.” |  |
| Sub-Clause 14.12 | Issue of Final Payment Certificate Design-Build In the first paragraph, “issue, to the Employer,” is replaced with “deliver, to the Employer and to the Contractor”. Further (a) is replaced with: “the amount which he fairly determines is finally due for the Design Build; and” |  |
| Sub-Clause 14.15 | Issue of Final Payment Certificate Operation Service In the first paragraph, “issue, to the Employer,” is replaced with “deliver, to the Employer and to the Contractor”. Further (a) is replaced with: “the amount which he fairly determines is finally due for the Operation Service; and; and (b) is replaced with: “the amount which he fairly determines is finally due for the Contract; and” |  |
| Sub- Clause 14.17 | Currencies of Payment In the first paragraph, “Unless otherwise stated in the Particular Conditions,” is deleted. |  |
| Sub-Clause 15.2 | Termination for Contractor’s Default The following is added as (h) before “or if any of the Contractor’s Personnel”: “(h) based on reasonable evidence, has engaged in Fraud and Corruption as defined in paragraph 2.2 of the Particular Conditions - Part C- Fraud and Corruption, in competing for or in executing the Contract.” Further in the second paragraph, “or (h)” is added after “or (g)” and paragraph (h) is renumbered (i). |  |
| Sub-Clause 15.5 | Termination for Employer’s Convenience The last paragraph is replaced with the following: “The Employer shall not terminate the Contract under this Sub-Clause in order to execute or operate the Works (or any part thereof) himself, or arrange for the Works (or any part thereof) to be executed or operated by another contractor, or to avoid a termination of the Contract by the Contractor under Clause 16.2 [Termination by Contractor]” |  |
| Sub-Clause 15.8 | Fraud and Corruption The following new Sub-Clause is added: “15.8.1 The Bank requires compliance with the Bank’s Anti-Corruption Guidelines and its prevailing sanctions policies and procedures as set forth in the Bank’s Sanctions Framework, as set forth in the Particular Conditions - Part C- Fraud and Corruption.”. 15.8.2 The Employer requires the Contractor to disclose any commissions or fees that may have been paid or are to be paid to agents or any other party with respect to the request for proposals process or execution of the Contract. The information disclosed must include at least the name and address of the agent or other party, the amount and currency, and the purpose of the commission, gratuity or fee.” |  |
| Sub-Clause 16.1 | Contractor’s Entitlement to Suspend Work The following paragraph added after the first paragraph: “Notwithstanding the above, if the Bank has suspended disbursements under the loan or credit from which payments to the Contractor are being made, in whole or in part, for the execution of the Works, and no alternative funds are available as provided for in Sub-Clause 2.4 [Employer’s Financial Arrangements], the Contractor may by Notice suspend work or reduce the rate of work at any time, but not less than 7 days after the Borrower having received the suspension notification from the Bank.” |  |
| Sub-Clause 16.2 | Termination by Contractor (d) is replaced with: “the Employer substantially fails to perform his obligations under the Contract in such manner as to materially and adversely affect the economic balance of the Contract and/or the ability of the Contractor to perform the Contract,” Further, the “or” is deleted at the end of sub-paragraph (f), and the following is added as a new sub-paragraph (h): “the Contractor does not receive the Employer’s Representative’s instruction recording the agreement of both Parties on the fulfilment of the conditions for the Commencement of Works under Sub-Clause 8.1 [Commencement of Works]. The following is added as penultimate paragraph: “In the event the Bank suspends the loan or credit from which part or whole of the payments to the Contractor are being made, if the Contractor has not received the sums due to him upon expiration of the 14 days referred to in Sub-Clause 14.8 [Payment] for payments under Interim Payment Certificates, the Contractor may, without prejudice to the Contractor's entitlement to financing charges under Sub-Clause 14.9 [Delayed Payment], take one of the following actions, namely (i) suspend work or reduce the rate of work under Sub-Clause 16.1, or (ii) terminate the Contract by giving notice to the Employer, with a copy to the Employer’s Representative, such termination to take effect 14 days after the giving of the notice.” |  |
| Sub-clause 16.3 | Cessation of Work and removal of Contractor’s Equipment In paragraph (b), the following is added after “received payment” “, including those items listed in the Employer’s Requirements”. |  |
| Sub-Clause 17.8 | Limitation of Liability: The sub-clause is replaced with the following: “Neither Party shall be liable to the other Party for loss of use of any Works, loss of profit, loss of any contract or for any indirect or consequential loss or damage which may be suffered by the other Party in connection with the Contract, other than as specifically provided in Sub-Clause 9.8 [Delay Damages relating to Design Build]; Sub-Clause 10.6 [Delays and Interruption during the Operation Service]; Sub-Clause 10.7 [Failure to Meet Performance Standards]; Sub-Clause 12.2 [Cost of Remedying Defects]; Sub-Clause 15.4 [Payment after Termination for Contractor’s Default]; Sub-Clause 16.4 [Payment on Termination]; Sub-Clause 17.9 [Indemnities by the Contractor]; Sub-Clause 17.10 [Indemnities by the Employer]; Sub-Clause 17.6(b) [Consequences of Employer’s Risks resulting in Damage] and Sub-Clause 17.12 [Risk of Infringement of Intellectual and Industrial Property Rights]. The total liability of the Contractor to the Employer, under or in connection with the Contract other than under Sub-Clause 4.19 [Electricity, Water and Gas], Sub-Clause 4.20 [Employer’s Equipment and Free-Issue Materials], Sub-Clause 17.1 [Indemnities] and Sub-Clause 17.5 [Intellectual and Industrial Property Rights], shall not exceed the sum resulting from the application of a multiplier (less or greater than one) to the Accepted Contract Amount, as stated in the Contract Data, or (if such multiplier or other sum is not so stated) the Accepted Contract Amount. This Sub-Clause shall not limit liability in any case of fraud, deliberate default or reckless misconduct by the defaulting Party.” |  |
| Sub-Clause 17.9 | Indemnities by the Contractor Sub-paragraph (b) is replaced with: “damage to or loss of any property, real or personal (other than the Works), to the extent that such damage or loss arises out of or in the course of or by reason of the design, the execution and completion or operation and maintenance of the Works, unless and to the extent that any such damage or loss is attributable to any negligence, willful act or breach of the Contract by the Employer, the Employer’s Personnel.” |  |
| Sub-Clause 17.13 | Use of Employer’s Accommodation/Facilities The following sub-clause added as 17.13: “Sub-Clause 17.13 - Use of Employer’s Accommodation/ Facilities The Contractor shall take full responsibility for the care of the Employer provided accommodation and facilities, if any, as detailed in the Employer’s Requirements, from the respective dates of hand-over to the Contractor until cessation of occupation (where hand-over or cessation of occupation may take place after the date stated in the Commissioning Certificate for the Works). If any loss or damage happens to any of the above items while the Contractor is responsible for their care arising from any cause whatsoever other than those for which the Employer is liable, the Contractor shall, at his own cost, rectify the loss or damage to the satisfaction of the Employer’s Representative.” |  |
| Sub-Clause 18.1 | Exceptional Risks The following added in (b) before “rebellion”: “sabotage by persons other than the Contractor’s Personnel,” Further in (c) and other employees of the Contractor and Subcontractors” is deleted. The following additional paragraphs are added at the end of the Sub-Clause: “(g) upstream pollution of the Influent that prevents the Contractor from providing the Operation Service in accordance with this Agreement. (h) if provided for in the Contract Data, events of high Influent turbidity in which the suspended solids exceed the value specified in the Contract Data and which prevent the Contractor from providing the Operation Service in accordance with this Agreement. [Only relevant for water treatment - provision to be deleted for wastewater treatment plant projects] (i) the wastewater Influent flow exceeds a capacity Performance Standard for the Works and prevents the Contractor from providing the Operation Service in accordance with this Agreement [provision to be deleted for water treatment plant projects]” |  |
| Sub-Clause 18.4 | Consequences of an Exceptional Event (b) is replaced with: “if the event or circumstance is of the kind described in sub-paragraphs (i) to (iv) of Sub-Clause 18.1 [Exceptional Risks] and, in sub-paragraphs (b) to (e), and (g) to (i), occurs in the Country, payment of any such Cost, including the costs of rectifying or replacing the Works and/or Goods damaged or destroyed by Exceptional Event, to the extent they are not recovered through the insurance policy referred to in Sub-Clause 19.2 [Insurances to be Provided by the Contractor during the Design-Build Period].” |  |
| Sub-Clause 18.56 | Optional Termination, Payment and Release In (c), “and necessarily” is inserted after “reasonably”. |  |
| Sub-Clause 19.1 | Insurance General Requirements After the fourth paragraph the following paragraph is added: “Wherever the Employer is the insuring Party, each insurance shall be effected with insurers and in terms acceptable to the Contractor. These terms shall be consistent with any terms agreed by both Parties before the date of the Letter of Acceptance. This agreement of terms shall take precedence over the provisions of this Clause.” Further the following is added as the final paragraph: “The Contractor shall be entitled to place all insurance relating to the Contract (including, but not limited to the insurance referred to Clause 19) with insurers from any eligible source country.” |  |
| Sub-Clause 19.2 | Insurances to be provided by the Contractor during the Design Build Period At the beginning of the Sub-Clause, add “unless otherwise stated in the Contract Data,” The following is added at the end of the Sub-Clause: “For those insurances required under this Sub-Clause to be in the joint names of the Parties, the Parties shall be jointly entitled to receive payments from the insurers, payments being held or allocated to the Party actually bearing the costs of rectifying the loss or damage,” |  |
| Sub-Clause 19.3 | Insurances to be provided by the Contractor during the Operation Service Period At the beginning of the Sub-Clause, add “unless otherwise stated in the Contract Data,” The following is added at the end of the Sub-Clause: “(f) Liability for breach of professional duty The Contractor shall insure the legal liability of the Contractor arising out of the negligent fault, defect, error or omission of the Contractor or any person for whom the Contractor is responsible in the carrying out their professional duties in an amount not less than that stated in the Contract Data. Such insurance shall contain an extension indemnifying the Contractor for his liability arising out of negligent fault, defect, error or omission in the carrying out his professional duties which result in the Works not being fit for the purpose specified in the Contract and resulting in any loss and/or damage to the Employer. The Contractor shall maintain this insurance for the period specified in the Contract Data. For those insurances required under this Sub-Clause to be in the joint names of the Parties, the Parties shall be jointly entitled to receive payments from the insurers, payments being held or allocated to the Party actually bearing the costs of rectifying the loss or damage.” |  |
| Sub-Clause 20.3 | Appointment of the Dispute Adjudication Board In the second paragraph, at the end of the first sentence after deleting: “.”, the following is added: “, each of whom shall meet the criteria set forth in Sub-Clause 3 of Appendix- General Conditions of Dispute Adjudication Agreement.” After the second paragraph, the following paragraph is inserted: “If the Contract is with a foreign Contractor, the DAB members shall not have the same nationality as the Employer or the Contractor.” |  |
| Sub-Clause 20.4 | Failure to Agree Dispute Adjudication Board In (a): “by the date stated in the first paragraph of Sub-Clause 20.3[Appointment of the Dispute Adjudication Board]” is replaced with: “within 42 days from the date the Contract is signed by both Parties”. In (b) and (c): “by such date” refers to “within 42 days from the date the Contract is signed by both Parties”. |  |
| Sub- Clause 20.8 | Arbitration In the first paragraph, delete starting from: “international arbitration” up to the end of (c), and is replaced with the following: “arbitration. Arbitration shall be conducted as follows: - if the contract is with foreign contractors, unless otherwise specified in the Contract Data; the dispute shall be finally settled under the Rules of Arbitration of the International Chamber of Commerce; by one or three arbitrators appointed in accordance with these Rules. The place of arbitration shall be the neutral location specified in the Contract Data; and the arbitration shall be conducted in the ruling language defined in Sub-Clause 1.4 [Law and Language]. (b) if the Contract is with domestic contractors, arbitration with proceedings conducted in accordance with the laws of the Employer’s country.” |  |
| General Conditions of Dispute Adjudication Agreement |  |  |
| 3.Warranties | The second paragraph starting “When appointing the Member” is replaced with: “When appointing the Member, each Party relies on the Member’s representations, that he/she; - has at least a bachelor’s degree in relevant disciplines such as law, engineering, construction management or contract management; - has at least ten years of experience in contract administration/management and dispute resolution, out of which at least five years of experience as an arbitrator or adjudicator in construction-related disputes; - has received formal training as an adjudicator from an internationally recognized organization; - has experience and/or is knowledgeable in the type of work which the Contractor is to carry out under the Contract; - has experience in the interpretation of construction and/or engineering contract documents; - has familiarity with the forms of contract published by FIDIC since 1999, and an understanding of the dispute resolution procedures contained therein; and - is fluent in the language for communications stated in the Contract Data (or the language as agreed between the Parties and the DAB).” |  |
| 6.Payments | From the paragraph starting with: “The Member shall submit invoices for”: “and air fares” and “other” are deleted from the first and second sentences respectively. |  |
| Procedural Rules for Dispute Adjudication Board members |  |  |
| Rule 10: “and” is deleted from (g) and the following is added: “and (i) appoint one or more experts (including legal and technical expert (s)), with the agreement of the Parties.” “Chairman” is replaced with “Chairperson”. |  |  |

Particular Conditions

Part C- Fraud and Corruption

(Text in this Particular Conditions - Part C shall not be modified)

1.	Purpose

1.1	The Bank’s Anti-Corruption Guidelines and this annex apply with respect to procurement under Bank Investment Project Financing operations.

2.	Requirements

2.1	The Bank requires that Borrowers (including beneficiaries of Bank financing); bidders, consultants, contractors and suppliers; any sub-contractors, sub-consultants, service providers or suppliers; any agents (whether declared or not); and any of their personnel, observe the highest standard of ethics during the procurement process, selection and contract execution of Bank-financed contracts, and refrain from Fraud and Corruption.

2.2	To this end, the Bank:

a.	Defines, for the purposes of this provision, the terms set forth below as follows:

i.	“corrupt practice” is the offering, giving, receiving, or soliciting, directly or indirectly, of anything of value to influence improperly the actions of another party;

ii.	“fraudulent practice” is any act or omission, including misrepresentation, that knowingly or recklessly misleads, or attempts to mislead, a party to obtain financial or other benefit or to avoid an obligation;

iii.	“collusive practice” is an arrangement between two or more parties designed to achieve an improper purpose, including to influence improperly the actions of another party;

iv.	“coercive practice” is impairing or harming, or threatening to impair or harm, directly or indirectly, any party or the property of the party to influence improperly the actions of a party;

v.	“obstructive practice” is:

(a)	deliberately destroying, falsifying, altering, or concealing of evidence material to the investigation or making false statements to investigators in order to materially impede a Bank investigation into allegations of a corrupt, fraudulent, coercive, or collusive practice; and/or threatening, harass or intimidating any party to prevent it from disclosing its knowledge of matters relevant to the investigation or from pursuing the investigation; or

(b)	acts intended to materially impede the exercise of the Bank’s inspection and audit rights provided for under paragraph 2.2 e. below.

b.	Rejects a proposal for award if the Bank determines that the firm or individual recommended for award, any of its personnel, or its agents, or its sub-consultants, sub-contractors, service providers, suppliers and/ or their employees, has, directly or indirectly, engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices in competing for the contract in question;

c.	In addition to the legal remedies set out in the relevant Legal Agreement, may take other appropriate actions, including declaring misprocurement, if the Bank determines at any time that representatives of the Borrower or of a recipient of any part of the proceeds of the loan engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices during the procurement process, selection and/or execution of the contract in question,  without the Borrower having taken timely and appropriate action satisfactory to the Bank to address such practices when they occur, including by failing to inform the Bank in a timely manner at the time  they knew of the practices;

d.	Pursuant to the Bank’s Anti- Corruption Guidelines and in accordance with the Bank’s prevailing sanctions policies and procedures, may sanction a firm or individual, either indefinitely or for a stated period of time, including by publicly declaring such firm or individual ineligible (i) to be awarded or otherwise benefit from a Bank-financed contract, financially or in any other manner;  (ii) to be a nominated  sub-contractor, consultant, manufacturer or supplier, or service provider of an otherwise eligible firm being awarded a Bank-financed contract; and (iii) to receive the proceeds of any loan made by the Bank or otherwise to participate further in the preparation or implementation of any Bank-financed project;

e.        Requires that a clause be included in bidding/request for proposals documents and in contracts financed by a Bank loan, requiring (i) bidders, consultants, contractors, and suppliers, and their sub-contractors, sub-consultants, service providers, suppliers, agents personnel, permit the Bank to inspect  all accounts, records and other documents relating to the submission of bids and contract performance, and to have them audited by auditors appointed by the Bank.

Particular Conditions

Part D- Environmental and Social (ES)

Metrics for Progress Reports

[Note to Employer: the following metrics may be amended to reflect the specifics of the Contract. The metrics that are required should be determined by the ES risks and impacts of the Works.]

Metrics for regular reporting:

              - environmental incidents or non-compliances with contract requirements, including contamination, pollution or damage to ground or water supplies;

              - health and safety incidents, accidents, injuries that require treatment and all fatalities;

              - interactions with regulators:  identify agency, dates, subjects, outcomes (report the negative if none);

              - status of all permits and agreements:

    - work permits: number required, number received, actions taken for those not received;

    - status of permits and consents:

  - list areas/facilities with permits required (quarries, asphalt & batch plants), dates of application, dates issued (actions to follow up if not issued), dates submitted to resident engineer (or equivalent), status of area (waiting for permits, working, abandoned without reclamation, decommissioning plan being implemented, etc.);

  - list areas with landowner agreements required (borrow and spoil areas, camp sites), dates of agreements, dates submitted to resident engineer (or equivalent);

  - identify major activities undertaken in each area in the reporting period and highlights of environmental and social protection (land clearing, boundary marking, topsoil salvage, traffic management, decommissioning planning, decommissioning implementation);

  - for quarries: status of relocation and compensation (completed, or details of activities and current status in the reporting period).

              - health and safety supervision:

- safety officer: number days worked, number of full inspections & partial inspections, reports to construction/project management;

- number of workers, work hours, metric of PPE use (percentage of workers with full personal protection equipment (PPE), partial, etc.), worker violations observed (by type of violation, PPE or otherwise), warnings given, repeat warnings given, follow-up actions taken (if any);

              - worker accommodations:

- number of expats housed in accommodations, number of locals;

- date of last inspection, and highlights of inspection including status of accommodations’ compliance with national and local law and good practice, including sanitation, space, etc.;

- actions taken to recommend/require improved conditions, or to improve conditions.

              - Health services: provider of health services, information and/or training, location of clinic, number of non-safety disease or illness treatments and diagnoses (no names to be provided);

              - gender (for expats and locals separately): number of female workers, percentage of workforce, gender issues raised and dealt with (cross-reference grievances or other sections as needed);

              - training:

- number of new workers, number receiving induction training, dates of induction training;

- number and dates of toolbox talks, number of workers receiving Occupational Health and Safety (OHS), environmental and social training;

- number and dates of communicable diseases (including STDs) sensitization and/or training, no. workers receiving training (in the reporting period and in the past); same questions for gender sensitization, flag person training.

- number and date of SEA and SH prevention sensitization and/or training events, including number of workers receiving training on Code of Conduct for Contractor’s Personnel (in the reporting period and in the past), etc.

              - environmental and social supervision:

- environmentalist: days worked, areas inspected and numbers of inspections of each (road section, work camp, accommodations, quarries, borrow areas, spoil areas, swamps, forest crossings, etc.), highlights of activities/findings (including violations of environmental and/or social best practices, actions taken), reports to environmental and/or social specialist/construction/site management;

- sociologist: days worked, number of partial and full site inspections (by area: road section, work camp, accommodations, quarries, borrow areas, spoil areas, clinic, HIV/AIDS center, community centers, etc.), highlights of activities (including violations of environmental and/or social requirements observed, actions taken), reports to environmental and/or social specialist/construction/site management; and

- community liaison person(s): days worked (hours community center open), number of people met, highlights of activities (issues raised, etc.), reports to environmental and/or social specialist /construction/site management.

              - Grievances: list new grievances (e.g. allegations of SEA and SH) received in the reporting period and unresolved past grievances by date received, complainant, how received, to whom referred to for action, resolution and date (if completed), data resolution reported to complainant, any required follow-up (Cross-reference other sections as needed):

- Worker grievances;

- Community grievances

              - l.	Traffic, road safety and vehicles/equipment:

- traffic and road safety incidents and accidents involving project vehicles & equipment: provide date, location, damage, cause, follow-up;

- traffic and road safety incidents and accidents involving non-project vehicles or property (also reported under immediate metrics): provide date, location, damage, cause, follow-up;

- overall condition of vehicles/equipment (subjective judgment by environmentalist); non-routine repairs and maintenance needed to improve safety and/or environmental performance (to control smoke, etc.).

              - Environmental mitigations and issues (what has been done):

- dust: number of working bowsers, number of waterings/day, number of complaints, warnings given by environmentalist, actions taken to resolve; highlights of quarry dust control (covers, sprays, operational status); % of rock/ spoil lorries with covers, actions taken for uncovered vehicles;

- erosion control: controls implemented by location, status of water crossings, environmentalist inspections and results, actions taken to resolve issues, emergency repairs needed to control erosion/sedimentation;

- quarries, borrow areas, spoil areas, asphalt plants, batch plants: identify major activities undertaken in the reporting period at each, and highlights of environmental and social protection: land clearing, boundary marking, topsoil salvage, traffic management, decommissioning planning, decommissioning implementation;

- blasting: number of blasts (and locations), status of implementation of blasting plan (including notices, evacuations, etc.), incidents of off-site damage or complaints (cross-reference other sections as needed);

- spill clean-ups, if any:  material spilled, location, amount, actions taken, material disposal (report all spills that result in water or soil contamination;

- waste management: types and quantities generated and managed, including amount taken offsite (and by whom) or reused/recycled/disposed on-site;

- details of tree plantings and other mitigations required undertaken in the reporting period;

- details of water and swamp protection mitigations required undertaken in the reporting period.

              - compliance:

- compliance status for conditions of all relevant consents/permits, for the Work, including quarries, etc.): statement of compliance or listing of issues and actions taken (or to be taken) to reach compliance;

- compliance status of C-ESMP/ESIP requirements: statement of compliance or listing of issues and actions taken (or to be taken) to reach compliance

- compliance status of SEA and SH prevention and response action plan: statement of compliance or listing of issues and actions taken (or to be taken) to reach compliance

- compliance status of Health and Safety Management Plan re: statement of compliance or listing of issues and actions taken (or to be taken) to reach compliance

- other unresolved issues from previous reporting periods related to environmental and social: continued violations, continued failure of equipment, continued lack of vehicle covers, spills not dealt with, continued compensation or blasting issues, etc.  Cross-reference other sections as needed

Section X – Contract Forms

## Table of Forms

Notification of Intention to Award	195

Beneficial Ownership Disclosure Form	199

Letter of Acceptance	201

Contract Agreement	202

Appendix 1 – Schedule of Payments	204

Appendix 2 – Schedule of Cost Indexation	205

Appendix 3 - Schedule of Performance Standards	208

Appendix 4 - Schedule of Performance Damages	211

Performance Security - Option 1: Demand Guarantee	212

Performance Security - Option 2: Performance Bond	214

Environmental and Social (ES) Performance Security	216

Advance Payment Security	218

Retention Money Security	220

# Notification of Intention to Award

[This Notification of Intention to Award shall be sent to each Proposer that submitted a Proposal, unless the Proposer has previously received notice of exclusion from the process at an interim stage of the procurement process.]

[Send this Notification to the Proposer’s Authorized Representative named in the Proposer Information Form]

For the attention of Proposer’s Authorized Representative

Name: [insert Authorized Representative’s name]

Address: [insert Authorized Representative’s Address]

Telephone/Fax numbers: [insert Authorized Representative’s telephone/fax numbers]

Email Address: [insert Authorized Representative’s email address]

[IMPORTANT: insert the date that this Notification is transmitted to all participating Proposers. The Notification must be sent to all Proposers simultaneously. This means on the same date and as close to the same time as possible.]

DATE OF TRANSMISSION: This Notification is sent by: [email/fax] on [date] (local time)

Notification of Intention to Award

Employer: [insert the name of the Employer]

Project: [insert name of project]

Contract title: [insert the name of the contract]

Country: [insert country where RFP is issued]

Loan No. /Credit No. / Grant No.: [insert reference number for loan/credit/grant]

RFP No: [insert RFP reference number from Procurement Plan]

This Notification of Intention to Award (Notification) notifies you of our decision to award the above contract. The transmission of this Notification begins the Standstill Period. During the Standstill Period you may:

- request a debriefing in relation to the evaluation of your Proposal, and/or

- submit a Procurement-related Complaint in relation to the decision to award the contract.

- The successful Proposer

| Name: | [insert name of successful Proposer] |
| --- | --- |
| Address: | [insert address of the successful Proposer] |
| Contract price: | [insert contract price of the successful Proposer] |
| Total combined score: | [insert the total combined score of the successful Proposer] |

- Other Proposers [INSTRUCTIONS: insert names of all Proposers that submitted a Proposal. If the Proposal’s price was evaluated include the evaluated price as well as the Proposal price as read out.]

| Name of Proposer | Technical Score | Proposal price | Evaluated Proposal Cost (if applicable) | Combined Score |
| --- | --- | --- | --- | --- |
| [insert name] | [insert Technical score] | [insert Proposal price] | [insert evaluated cost] | [insert combined score] |
| [insert name] | [insert Technical score] | [insert Proposal price] | [insert evaluated cost] | [insert combined score] |
| [insert name] | [insert Technical score] | [insert Proposal price] | [insert evaluated cost] | [insert combined score] |
| [insert name] | [insert Technical score] | [insert Proposal price] | [insert evaluated cost] | [insert combined score] |
| [insert name] | [insert Technical score] | [insert Proposal price] | [insert evaluated cost] | [insert combined score] |

- Reason/s why your Proposal was unsuccessful [Delete if the combined score already reveals the reason]

[INSTRUCTIONS; State the reason/s why this Proposer’s Proposal was unsuccessful. Do NOT include: (a) a point by point comparison with another Proposer’s Proposal or (b) information that is marked confidential by the Proposer in its Proposal.]

- How to request a debriefing

DEADLINE: The deadline to request a debriefing expires at midnight on [insert date] (local time). You may request a debriefing in relation to the results of the evaluation of your Proposal. If you decide to request a debriefing your written request must be made within three (3) Business Days of receipt of this Notification of Intention to Award. Provide the contract name, reference number, name of the Proposer, contact details; and address the request for debriefing as follows: Attention: [insert full name of person, if applicable] Title/position: [insert title/position] Agency: [insert name of Employer] Email address: [insert email address] Fax number: [insert fax number] delete if not used If your request for a debriefing is received within the 3 Business Days deadline, we will provide the debriefing within five (5) Business Days of receipt of your request. If we are unable to provide the debriefing within this period, the Standstill Period shall be extended by five (5) Business Days after the date that the debriefing is provided. If this happens, we will notify you and confirm the date that the extended Standstill Period will end. The debriefing may be in writing, by phone, video conference call or in person. We shall promptly advise you in writing how the debriefing will take place and confirm the date and time. If the deadline to request a debriefing has expired, you may still request a debriefing. In this case, we will provide the debriefing as soon as practicable, and normally no later than fifteen (15) Business Days from the date of publication of the Contract Award Notice.

- How to make a complaint

DEADLINE: The deadline for submitting a Procurement-related Complaint challenging the decision to award the contract expires on midnight, [insert date] (local time). Provide the contract name, reference number, name of the Proposer, contact details; and address the Procurement-related Complaint as follows: Attention: [insert full name of person, if applicable] Title/position: [insert title/position] Agency: [insert name of Employer] Email address: [insert email address] Fax number: [insert fax number] delete if not used At this point in the procurement process, you may submit a Procurement-related Complaint challenging the decision to award the contract. You do not need to have requested, or received, a debriefing before making this complaint. Your complaint must be submitted within the Standstill Period and received by us before the Standstill Period ends. Further information: For more information, see the “Procurement Regulations for IPF Borrowers (Procurement Regulations) (Annex III).” You should read these provisions before preparing and submitting your complaint. In addition, the World Bank’s Guidance “How to make a Procurement-related Complaint” provides a useful explanation of the process, as well as a sample letter of complaint. In summary, there are four essential requirements: - You must be an ‘interested party’. In this case, that means a Proposer who submitted a Proposal in this procurement, and is the recipient of a Notification of Intention to Award. - The complaint can only challenge the decision to award the contract. - You must submit the complaint within the deadline stated above. - You must include, in your complaint, all of the information required by the Procurement Regulations (as described in Annex III).

- Standstill Period

DEADLINE: The Standstill Period is due to end at midnight on [insert date] (local time). The Standstill Period lasts ten (10) Business Days after the date of transmission of this Notification of Intention to Award. The Standstill Period may be extended. This may happen where we are unable to provide a debriefing within the five (5) Business Day deadline. If this happens we will notify you of the extension.

If you have any questions regarding this Notification, please do not hesitate to contact us.

On behalf of the Employer:

Signature: 	______________________________________________

Name:	______________________________________________

Title/position:	______________________________________________

Telephone:	______________________________________________

Email:	______________________________________________

INSTRUCTIONS TO PROPOSERS: DELETE THIS BOX ONCE YOU HAVE COMPLETED THE FORM

This Beneficial Ownership Disclosure Form (“Form”) is to be completed by the successful Proposer.  In case of joint venture, the Proposer must submit a separate Form for each member.  The beneficial ownership information to be submitted in this Form shall be current as of the date of its submission.

For the purposes of this Form, a Beneficial Owner of a Proposer is any natural person who ultimately owns or controls the Proposer by meeting one or more of the following conditions:

- directly or indirectly holding 25% or more of the shares

- directly or indirectly holding 25% or more of the voting rights

- directly or indirectly having the right to appoint a majority of the board of directors or equivalent governing body of the Proposer

Beneficial Ownership Disclosure Form

RFP No.: [insert number of RFP process]

Request for Proposal No.: [insert identification]

To: [insert complete name of Employer]

In response to your request in the Letter of Acceptance dated [insert date of letter of Acceptance] to furnish additional information on beneficial ownership: [select one option as applicable and delete the options that are not applicable]

(i) we hereby provide the following beneficial ownership information.

Details of beneficial ownership

| Identity of Beneficial Owner | Directly or indirectly holding 25% or more of the shares (Yes / No) | Directly or indirectly holding 25 % or more of the Voting Rights (Yes / No) | Directly or indirectly having the right to appoint a majority of the board of the directors or an equivalent governing body of the Proposer (Yes / No) |
| --- | --- | --- | --- |
| [include full name (last, middle, first), nationality, country of residence] |  |  |  |

OR

(ii) We declare that there is no Beneficial Owner meeting one or more of the following conditions:

- directly or indirectly holding 25% or more of the shares

- directly or indirectly holding 25% or more of the voting rights

- directly or indirectly having the right to appoint a majority of the board of directors or equivalent governing body of the Proposer

OR

(iii) We declare that we are unable to identify any Beneficial Owner meeting one or more of the following conditions. [If this option is selected, the Proposer shall provide explanation on why it is unable to identify any Beneficial Owner]

- directly or indirectly holding 25% or more of the shares

- directly or indirectly holding 25% or more of the voting rights

- directly or indirectly having the right to appoint a majority of the board of directors or equivalent governing body of the Proposer]”

Name of the Proposer: *[insert complete name of the Proposer]_________

Name of the person duly authorized to sign the Proposal on behalf of the Proposer: **[insert complete name of person duly authorized to sign the Proposal]___________

Title of the person signing the Proposal: [insert complete title of the person signing the Proposal]______

Signature of the person named above: [insert signature of person whose name and capacity are shown above]_____

Date signed [insert date of signing] day of [insert month], [insert year]_____

* In the case of the Proposal submitted by a Joint Venture specify the name of the Joint Venture as Proposer. In the event that the Proposer is a joint venture, each reference to “Proposer” in the Beneficial Ownership Disclosure Form (including this Introduction thereto) shall be read to refer to the joint venture member.

** Person signing the Proposal shall have the power of attorney given by the Proposer. The power of attorney shall be attached with the Proposal Schedules.

# Letter of Acceptance

[letterhead paper of the Employer]

[date]

To: [name and address of the Contractor]

This is to notify you that your Proposal dated [date] for execution of the [name of the Contract and identification number, as given in the Contract Data] for the Accepted Contract Amount [amount in numbers and words] [name of currency], as corrected and modified in accordance with the Instructions to Proposers, is hereby accepted by our Agency.

The amount is made up of the following components:

| The Accepted Contract Amount for the Design-Build of: | ……………………………………… (currency and amount in figures) |
| --- | --- |
| The Accepted Contract Amount for the Operation Service* of: | ……………………………………… (currency and amount in figures) |

*Insert value including amounts for asset replacement

You are requested to furnish (i) the Performance Security and an Environmental and Social Performance Security [Delete ES Performance Security if it is not required under the contract] within 28 days in accordance with the Conditions of Contract, using for that purpose one of the Performance Security and an Environmental and Social Performance Security Forms [Delete ES Performance Security if it is not required under the contract] and (ii) the additional information on beneficial ownership in accordance with PDS ITP 53.1, within eight (8) Business days using the Beneficial Ownership Disclosure Form, included in Section X, Contract Forms, of the request for proposals document.

Authorized Signature:

Name and Title of Signatory:

Name of Agency:

Attachment: Contract Agreement

# Contract Agreement

THIS AGREEMENT made the ________ day of ________________________, _____, between ______________________________________of __________________________ (hereinafter “the Employer”), of the one part, and ______________________ of _____________________ (hereinafter “the Contractor”), of the other part:

WHEREAS the Employer desires that the Works known as _____________________________ _______________________________ should be designed, executed and operated by the Contractor, and has accepted a Proposal by the Contractor for the design, execution, completion and operation and maintenance of these Works and the remedying of any defects therein,

The Employer and the Contractor agree as follows:

1.	In this Agreement words and expressions shall have the same meanings as are respectively assigned to them in the Contract documents referred to.

2.	The following documents shall be deemed to form and be read and construed as part of this Agreement. This Agreement shall prevail over all other Contract documents.

- the Letter of Acceptance

- the Letter of Proposal

- the addenda Nos _______(if any)

- the Particular Conditions

- the General Conditions

- the Employer’s Requirements

- the completed Schedules,

- The Operating License and

- The Contractor’s Proposal and any other documents forming part of the Contract

including, but not limited to:

    - Code of Conduct for Contractor’s Personnel (ES).

3.	In consideration of the payments to be made by the Employer to the Contractor as specified in this Agreement, the Contractor hereby covenants with the Employer to design, execute, complete, operate and maintain the Works and to remedy defects therein in conformity in all respects with the provisions of the Contract and Operating License.

4.	The Employer hereby covenants to pay the Contractor in consideration of the design, execution, completion operation and maintenance of the Works and the remedying of defects therein, the Contract Price, or such other sum as may become payable under the provisions of the Contract, at the times and in the manner prescribed by the Contract and to grant the Contractor (or cause the Contractor to be granted) a royalty-free license to enable him to operate and maintain the Works during the Operation Service Period

IN WITNESS whereof the parties hereto have caused this Agreement to be executed in accordance with the laws of _____________________________ on the day, month and year specified above.

Signed by ________________________________________________ (for the Employer)

Signed by ________________________________________________ (for the Contractor)

Appendices to the Contract Agreement:

Appendix 1: Schedule of Payments

Appendix 2: Schedule of Cost Indexation( Not Applicable)

Appendix 3: Schedule of Performance Standards

Appendix 4: Schedule of Performance Damages

# Appendix 1 – Schedule of Payments

|  | Payment Schedule |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Major Work Activity | Type of Payment |  | Payment (in % of Total Price) | Amount | Cumulative % |
| 0 | Advance Payment | 15% of the Accepted Contract Amount for the Design Build payable in the currencies and proportions in which the Accepted Contract Amount for Design Build is payable against an un conditional Bank Guarantee. The advance payment shall be repaid through percentage deductions in Interim Payment Certificates. Unless other percentages are stated in the Contract Data: - deductions shall commence in the Interim Payment Certificate in which the total of all certified interim payments (excluding the advance payment and deductions and repayments of retention) exceeds ten percent (10%) of the Accepted Contract Amount for the Design-Build less Provisional Sums; and - deductions shall be made at the amortization rate of one-quarter (25%) of the amount of each Interim Payment Certificate (excluding the advance payment and deductions and repayments of retention) issued during the Design-Build Period. |  |  |  |  |
| 1 | Activity 1 Design and Documentation |  |  |  |  |  |
| 1.1. | Final Design and Documentation Design Report (calculations, copies of relevant design manuals, standard etc) Construction Drawings etc on submission | LS |  | 90% |  |  |
| 1-2 | Ditto on Approvals | LS |  | 10% |  |  |
| 2 | Activity 2: Mobilization and Submittals |  |  |  |  |  |
| 2.1 | Mobilization: Preparation of construction site. mobilization of contractor’s site staff, topographical surveys, subsoil investigation, contractor’s and employer’ office and utility connections &etc. | LS |  | 90% |  |  |
| 2.2 | Submittals: Contractor’s programme, Project specific quality plan(D&B), Occupational Health, Safety and Environmental Management Plan and Others as specified in the Contract. | LS |  | 10% |  |  |
| 3 | Activity 3: Construction-Civil Works |  |  |  |  |  |
| 3-1 | Water Retaining Structures (e.g. Pre Treatment, Biological Treatment, Tertiary Treatment, Sludge Treatment, Sewage Diversion from Phase 1 area, Emergency outfall etc) (Bidder shall expand this to suit the treatment process he adopts). | P |  | 90 % |  |  |
| 3-2 | Water Retaining Structures after Hydraulic Testing | P |  | 5% |  |  |
| 3-3 | Water Retaining Structures after successful completion of testing, trial run, and performance guarantee test | LS |  | 5% |  |  |
| 3-4 | Non Water Retaining Structures (Like Pump House, In Vessel Composting Plant building, Electrical Panel Room Blower Room, Admin Building, Laboratory, Roads, Drains Pathways, Landscaping& Tree planting, etc). ) (Bidder shall expand this to suit) | P |  | 95% |  |  |
| 3-5 | Non Water Retaining Structures On completion of work & putting the plant/unit in to full service. | LS |  | 5% |  |  |
|  | Activity 4: Mechanical & Electrical. Instrumentation Plant and Equipment for Incorporation in the Permanent Works Including In Vessel Composting Plan and trial run |  |  |  |  |  |
| 4.1 | M&E and ancillary equipment required for incorporation in the Permanent works. Procure and Supply all Mechanical and Electrical Equipment, Instrumentation, Automation etc required for the Works. |  | P | 70% |  |  |
| 4.2 | Completion of installation: Installation of all the M&E and ancillary equipment on site. |  | P | 20 % |  |  |
| 4.3 | Completion of Testing: Successful completion of testing, trial run, commissioning and performance guarantee test |  | LS | 10 % |  |  |
| 5 | Operation and Maintenance during Ten (10) Years Period |  |  |  |  |  |
| 5-1 | Monthly O&M Services (On completion of each month’s operations and maintenance) inclusive of man power, consumables & preventive maintenance/replacement during 10 year maintenance period. |  | P | 100 % |  |  |

# Appendix 2 – Schedule of Cost Indexation

1.	General requirements

To the extent, that the Contract Data allows for price adjustment, the amounts payable to the Contractor shall be adjusted for rises or falls in the cost of labour, goods and other inputs to the Works or Operation Service by the addition or deduction of the amounts determined by the formulae prescribed in this Appendix. To the extent that full compensation for any rise or fall in costs is not covered by the provisions of this or other Clauses, the Accepted Contract Amount shall be deemed to have included amounts to cover the contingency of other rises and falls in costs.

The adjustment to be applied to the amount otherwise payable to the Contractor, as valued in accordance with the appropriate Schedule and certified in Payment Certificates, shall be determined from formulae for each of the currencies in which the Contract Price is payable. No adjustment is to be applied to work valued on the basis of Cost or current prices.

2.	Adjustment of Design-Build Prices (Not Applicable)

3.	Adjustment of Operation Service amounts (excluding Asset Replacement)

[In most cases the operation service fees will be paid in local currency and the general type of formula indicated below can be adopted. The formula and associated schedules will require adjustment if the Employer intends to allow payment in foreign currency or allow more than one index per foreign currency. Separate indexation provisions may be required for each component of the operation service fee.]

If the Contract Data allows for price adjustment of Operation Service amounts, the formulae shall be of the following general type:

Pn= 	b Ln/lo + c En/Eo + d Mn/Mo + ......

+ w [Rate(Fc1)n / Rate(Fc1)o] x [ Ind(Fc1)n / Ind(Fc1)o]

+ y [Rate(Fc2)n / Rate(Fc2)o] x [ Ind(Fc2)n / Ind(Fc2)o]

+ z ……

where:

“Pn” is the adjustment multiplier to be applied to the local currency amount in period “n”, this period being a month unless otherwise stated in the Appendix to Proposal;

“b”, “c”, “d”, ... are coefficients representing the estimated proportion of each cost element related to local currency in the relevant table of adjustment data; such tabulated cost elements may be indicative of resources such as labour, equipment and materials;

“Ln”, “En”, “Mn”, ... are the local currency current cost indices or reference prices for period “n”, each of which is applicable to the relevant tabulated cost element on the date 49 days prior to the last day of the period to which the particular Payment Certificate relates;

“Lo”, “Eo”, “Mo”, ... are the local currency base cost indices or reference prices, each of which is applicable to the relevant tabulated cost element on the Base Date.

“w”, “y”, “z” ... are coefficients representing the estimated proportion of each cost element related to foreign currencies as stated in the relevant table of adjustment data; such tabulated cost elements may be indicative of resources such as labour, equipment and materials;

“Rate(Fc1)n”, “Rate (Fc2)n” are the foreign currency exchange rates which are applicable to the relevant tabulated cost element on the date 49 days prior to the last day of the period to which the particular Payment Certificate relates;

“Rate (Fc1)o”, “Rate (Fc2)o” ….. are the foreign currency exchange rates on the base date;

“Ind(Fc1)n” “Ind(Fc2)n” …. are the foreign currency current cost indices for period “n” on the date 49 days prior to the last day of the period to which the particular Payment Certificate relates;

“Ind(Fc1)o” “Ind(Fc2)o” …… are the foreign currency cost indices on the base date.

Exchange rates in the above formulae shall be the selling rate, established by the central bank of the Country of the currency under consideration, on the date for which the index is required to be applicable.

4.	Adjustment of Asset Replacement amounts

[In most cases the asset replacement amounts will be paid in local currency. The formula will require adjustment if the Employer intends to allow payment in foreign currency or allow more than one index per foreign currency.]

If the contract data allows for price adjustment of asset replacement amounts, the formulae shall be of the following general type:

Pn= 	q [Ind(LC)n/ Ind(LC)o] + r [Rate(Fc1)n / Rate(Fc1)o] x [Ind(Fc1)n/Ind(Fc1)o] +

+ s [ etc…….

where:

“Pn” is the adjustment multiplier to be applied to the total (in local currency) indicated in column [d] of the Asset Replacement schedule.

“q”, “r”, “s”, ... are coefficients representing the estimated proportion of each cost element related to different currencies of payment indicated in the Asset Replacement Schedule; such tabulated cost elements may be indicative of resources such as labour, equipment and materials;

Ind(LC)n is the local currency cost index for period “n” on the date 49 days prior to the last day of the period to which the particular Payment Certificate relates;

Ind(LC)o is the local currency cost index on the base date;

Rate(Fc1)n , Rate(Fc1)o, Ind(Fc1)n and Ind(Fc1)o ….etc. have the meanings ascribed above in sub-section 3 of this schedule of adjustment data [adjustment of Operation Service amounts].

# Appendix 3 - Schedule of Performance Standards

Examples:

1. Capacity Standard (s)

| No | Item | Unit | Minimum Capacity |
| --- | --- | --- | --- |
| 1 | Design capacity (Flow) | MLD | 10.00 (Average Flow) |

Allowable Exclusions (if any):

- The Contractor shall design and build the Works to meet the minimum capacity requirements specified in the employers requirements, and shall ensure that such capacity is available throughout the Operation Service Period.

- The Plant shall never be operated at less than 50% of its design capacity due to maintenance and repair reasons. The period of such exceptional operation shall not exceed two consecutive days and shall not be more than three days a week. The maximum downtime of the whole Plant shall not exceed 8 hours. The periods for repairs and maintenance have to be communicated to the Engineer-In-Charge at least one month in advance. For machinery and equipment which requires maintenance to be carried out by manufacturer/ manufacturer’s authorized representative, the down time shall not exceed 30 days. Employer reserves the right to impose penalty, should there be any default by Contractor on this account. The penalty per day shall be 1% of O&M monthly payment beyond the permitted downtime. The penalty amount will be deducted in the subsequent O&M bill if adequate reasons are not furnished by the Contractor for delay.

2. Reliability Standards (unscheduled interruptions/downtime)

| No | Item | Unit | Value |
| --- | --- | --- | --- |
| 1 | Critical Equipment / Instrumentation (Critical equipment shall mean those equipment’s / systems which are essential to ensure the plants performance and it shall include all flow and treated water quality measuring instruments and systems including submersible mixers, blowers, sludge and MLSS recirculation pumps, disinfection (chlorination system), filters electrical systems such as critical electrical system such transformers, electrical panels etc.) | beyond X hours i.e. X hours | X=48 |
| 2 | Semi-Critical Equipment Semi Critical equipment shall mean those equipment’s / systems which are normally necessary to ensure the plants performance and they shall include all screens, grit removal systems, primary clarifiers, bio reactors (aeration system), secondary clarifiers, sludge thickening, and digestion systems etc. | Beyond Y days | Y= 7 |
| 3 | Non Critical Equipment Non Critical equipment shall mean those equipment’s/ systems which have been provided at the plant are but are not critical in for delivering the plants performance, such as area lighting, air conditioners, Instruments not critical towards operation of the plant. | Beyond Z days | Z= 10 |
| 4 | Safety Equipment Not using PPE (Personal Protective Equipment) devices, Non compliance to Occupational Safety, Health & Environment guidelines, Non Compliance to respective government agencies in O&M of STP | occurrences/Month | Up to 2 |
|  |  | Occurrences/Month | >2 & up to 5 |
|  |  | Occurrences/Month | >5 & up to 10 |
|  |  | occurrences/Month | Above 10 |

Allowable Exclusions (if any):

- [list – e.g. interruptions caused by third parties]

Note: The Contractor will not be held responsible for interruptions to the sewage treatment process as a result of Grid power failures (unless as a result of a Plant failure) interruptions in the raw Sewage supply etc. which are out of his control. However, the Contractor shall be required to demonstrate that the Works can cope with these inevitable interruptions in an orderly fashion and recover to a normal operational state with the minimum of manual intervention. All consumables except power needed for operation of the Works and transportation of sludge off site shall be provided by the Contractor. The Contractor shall provide all facilities and equipment not supplied under the contract and which are deemed necessary for the Contractor to carry out and monitor the Tests after Completion

3. Water Quality / Effluent Discharge Standards ((to comply EPA’s Requirements in Table 6.3 National Water Quality Guidelines, Ground Water Recharge.)

| No | Parameter | Unit | Maximum Concentration or Limit |
| --- | --- | --- | --- |
| 1 | pH |  | 5-9.5 |
| 2 | BOD | mg/l | 5 |
| 3 | COD | mg/l | 5 |
| 4 | TSS | mg/l | 15 |
| 5 | Nitrates | mg/l | 6 |
| 6 | Fecal Coliforms | org/ml | 10 org / 100 ml |
| 7 | E. Coliforms | org/ml | 0 org / 100 ml |
| 8 | Residual Chlorine | org/ml | 0.2-0.8 mg/l |
| 9 | Dissolved oxygen | mg/l | 2.0 |
| 10 | Conductivity |  | Equal or less than receiving ground water |
| 11 | Oil, grease and waxes (food related) | mg/l | <5 |

Allowable Exclusions (if any): None

4. Sludge standards

| No | Parameter | Unit | Value / Limit |
| --- | --- | --- | --- |
| 1 | Minimum sludge TSS (dry solids) | % w/w | 25% |
| 2 | Maximum use of Polyelectrolyte | Kg | 2.5 Kg/T of dry solids |

Allowable Exclusions (if any): None

5. Smell and Noise Standards

| No | Item | Unit | Limit |
| --- | --- | --- | --- |
| Smell Standard |  |  |  |
| 1 | Odour at boundary |  | No Odour |
| Noise standards |  |  |  |
| 1 | All rotating equipment not having reciprocating parts with motor kW less | dBAat 1.00 m from equipment | 85 |
| 2 | All rotating equipment not having reciprocating parts with motor kW less | (mm/sec) | 1.12 |
| 3 | All rotating equipment not having reciprocating parts with motor kW more than 15 kW and less than or equal to 75 kW | dBAat 1.00 m from equipment | 85 |
| 4 | All rotating equipment not having reciprocating parts with motor kW more than 15 kW and less than or equal to 75 kW | (mm/sec) | 1.8 |
| 5 | All rotating equipment not having reciprocating parts with motor kW greater than 75 kW | dBAat 1.00 m from equipment | 85 |
| 6 | All rotating equipment not having reciprocating parts with motor kW greater than 75 kW | (mm/sec) | 2.8 |
| 7 | All equipment having reciprocating parts viz. compressors, dosing pumps sampling pumps | dBAat 1.00 m from equipment | 85 |

Allowable Exclusions (if any): None

6. Monitoring and testing standards

| No | Parameter | Type of test | Frequency of testing |
| --- | --- | --- | --- |
| 1 | BOD5 | 24-hour flow proportional samples | Daily |
| 2 | Chemical Oxygen Demand | 24-hour flow proportional samples | Weekly |
| 3 | Total suspended solids | 24-hour flow proportional samples | Daily |
| 4 | Sludge | Grab Samples | Weekly |
| 5 | Treated Effluent Fecal Coliform | Composite sample | Daily |

Allowable exclusions (if any): None

7. Energy efficiency standards (required for short and medium term DBOs)

| No | Efficiency item | Unit | Limit Value (maximum permitted average energy use during evaluation period) | Efficiency evaluation period |
| --- | --- | --- | --- | --- |
| 1 | STP including pumping station capacity (Cum/day) | cum/day | Not more than:0.561 KWH/per cubic meter (cum) of plant effluent | - Quarterly |

Allowable exclusions (if any): None

8. Chemical efficiency standards (required for short and medium term DBOs)

| No | Efficiency item | Unit | Limit Value (maximum permitted average chemical use during evaluation period) | Efficiency evaluation period |
| --- | --- | --- | --- | --- |
| 1 | The consumption of Chlorine during the Tests after Completion is guaranteed to be: | Kg per M3 of effluent produced | Not more than:.0.0008kg per cubic meter (cum) of plant effluent | - Monthly |
| 2 | The consumption of dewatering Polymer (polyelectrolyte)during the Tests after Completion is guaranteed to be | Kg per M3 of effluent produced | Not more than:0.0025kg per cubic meter (cum) of plant effluent | - Monthly |

(required for shorter term DBOs)

Allowable exclusions (if any): None

# Appendix 4 - Schedule of Performance Damages

The Contractor shall pay to the Employer performance damages in accordance with GC Sub-Clauses 10.6 and 10.7 in the amounts specified below.

Performance Damages for Delay and Interruptions

| Ref: | Item | Unit [e.g. amount per day, per incident etc.] | Insert amount [either as an amount in currency or as percentage of Accepted Contract Amount for Design-Build] |
| --- | --- | --- | --- |
| As Included in appropriate section of Appendix 3 |  |  |  |
| 1 | Critical Equipment / Instrumentation (Critical equipment shall mean those equipment’s / systems which are essential to ensure the plants performance and it shall include all flow and treated water quality measuring instruments and systems including submersible mixers, blowers, sludge and MLSS recirculation pumps, disinfection (chlorination system), filters electrical systems such as critical electrical system such transformers, electrical panels etc.) | beyond 48 hours i.e. 48 hours | 3% of Monthly O&M Cost per day of default beyond permitted breakdown time period |
| 2 | Semi-Critical Equipment Semi Critical equipment shall mean those equipment’s / systems which are normally necessary to ensure the plants performance and they shall include all screens, grit removal systems, primary clarifiers, bio reactors (aeration system), secondary clarifiers, sludge thickening, and digestion systems etc. | Beyond 7 days | 2% of Monthly O&M Cost per day of default beyond permitted breakdown time period |
| 3 | Non Critical Equipment Non Critical equipment shall mean those equipment’s/ systems which have been provided at the plant are but are not critical in for delivering the plants performance, such as area lighting, air conditioners, Instruments not critical towards operation of the plant. | Beyond 10 days | 1% of Monthly O&M Cost per day of default beyond permitted breakdown time period |
| 4 | Safety Equipment Not using PPE (Personal Protective Equipment) devices, Non compliance to Occupational Safety, Health & Environment guidelines, Non Compliance to respective government agencies in O&M of STP | Up to 2 occurrences/Month | No Penalty |
|  |  | >2 & up to 5 Occurrences/Month | MVR 250 per occurrence |
|  |  | >5 & up to 10 Occurrences/Month | MVR 1250 occurrence |
|  |  | Above 10 occurrences/Month | MVR 2500 per complaint or termination of Contract |

Performance Damages for failure to meet Performance Standards

| Ref: |  | Item |  | Unit [e.g. amount per day, per incident, per cubic meter, etc.] |  |  |  |  | Insert amount [either as an amount in currency or as percentage of Accepted Contract Amount for Design-Build] |  |  |  |  |  | Exclusions (if any) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Water Quality / Effluent Discharge Standards |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No |  | Parameter |  | Unit |  |  |  | Maximum Concentration or Limit |  |  |  |  | Measured Parameter in excess of Specified maximum |  | Penalty/day as % of O&M Monthly Payment |
| 1 |  | pH |  |  |  |  |  | 5-9.5 |  |  |  |  | NA |  | NA |
| 2 |  | BOD |  | mg/l |  |  |  | 5 |  |  |  |  | 2mg/l BOD |  | 1% |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 3mg/l, BOD |  | 1.5% |
|  |  |  |  |  |  |  |  |  |  |  |  |  | >3mg/l, BOD |  | 2.5% |
| 3 |  | COD |  | mg/l |  |  |  | 50 |  |  |  |  | NA |  | NA |
| 4 |  | TSS |  | mg/l |  |  |  | 15 |  |  |  |  | 3 mg/l, TSS |  | 1% |
|  |  |  |  |  |  |  |  |  |  |  |  |  | >3mg/l, TSS |  | 2.5% |
| 5 |  | Total Nitrogen |  | mg/l |  |  |  | 10 |  |  |  |  | 3 mg/l TN |  | 1% |
|  |  |  |  |  |  |  |  |  |  |  |  |  | >3mg/l, TN |  | 2% |
| 6 |  | Fecal Coliforms |  | org/ml |  |  |  | 10 org / 100 ml |  |  |  |  | >10 org/100ml |  | 1% |
| 7 |  | E. Coliforms |  | org/ml |  |  |  | 0 org / 100 ml |  |  |  |  | >0 org/100ml |  | 1% |
| 8 |  | Residual Chlorine |  | mg/l |  |  |  | 0.2-0.8 mg/l |  |  |  |  | < 0.2 mg/l |  | 1% |
| 9 |  | Dissolved oxygen |  | mg/l |  |  |  | 2.0 |  |  |  |  | <2.0 mg/l |  | 1% |
| 10 |  | Conductivity |  |  |  |  |  | Equal or less than receiving ground water |  |  |  |  | NA |  | NA |
| 11 |  | Oil, grease and waxes (food related) |  | mg/l |  |  |  | <5 |  |  |  |  | 2mg/l Oil& Grease |  | 1% |
|  |  |  |  |  |  |  |  |  |  |  |  |  | >2mg/l Oil& Grease |  | 2% |
| Sludge standards |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No |  | Parameter |  |  | Unit |  |  | Value / Limit |  |  |  |  | Number of days for which parameters were not met |  | Penalty |
| 1 |  | Minimum sludge TSS (dry solids) |  |  | % w/w |  |  | 25% |  |  |  |  | X |  | (X) x0.005% of monthly running charges per day |
| 2 |  | Maximum use of Polyelectrolyte |  |  | Kg |  |  | 2.5 Kg/T of dry solids |  |  |  |  | X |  | (X) x0.005% of monthly running charges per day |
| Smell and Noise Standards |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No |  | Item |  |  | Unit |  |  | Limit |  |  |  | Number of days for which parameters were not met |  |  | Penalty |
| 1 |  | Odour at boundary |  |  |  |  |  | No Odour |  |  |  | X |  |  | (X) x0.005% of monthly running charges per day |
| 1 |  | All rotating equipment not having reciprocating parts with motor kW less |  |  | dBAat 1.00 m from equipment |  |  | 85 |  |  |  | X |  |  | (X) x0.001% of monthly running charges per day |
| 2 |  | All rotating equipment not having reciprocating parts with motor kW less |  |  | (mm/sec) |  |  | 1.12 |  |  |  | X |  |  | (X) x0.001% of monthly running charges per day |
| 3 |  | All rotating equipment not having reciprocating parts with motor kW more than 15 kW and less than or equal to 75 kW |  |  | dBAat 1.00 m from equipment |  |  | 85 |  |  |  | X |  |  | (X) x0.001% of monthly running charges per day |
| 4 |  | All rotating equipment not having reciprocating parts with motor kW more than 15 kW and less than or equal to 75 kW |  |  | (mm/sec) |  |  | 1.8 |  |  |  | X |  |  | (X) x0.001% of monthly running charges per day |
| 5 |  | All rotating equipment not having reciprocating parts with motor kW greater than 75 kW |  |  | dBAat 1.00 m from equipment |  |  | 85 |  |  |  | X |  |  | (X) x0.001% of monthly running charges per day |
| 6 |  | All rotating equipment not having reciprocating parts with motor kW greater than 75 kW |  |  | (mm/sec) |  |  | 2.8 |  |  |  | X |  |  | (X) x0.001% of monthly running charges per day |
| 7 |  | All equipment having reciprocating parts viz. compressors, dosing pumps sampling pumps |  |  | dBAat 1.00 m from equipment |  |  | 85 |  |  |  | X |  |  | (X) x0.001% of monthly running charges per day |
| Energy efficiency standards |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No | Efficiency item |  | Unit |  |  | Limit Value (maximum permitted average energy use during evaluation period) |  |  |  | Efficiency evaluation period |  |  |  | Penalty |  |
| 1 | STP including pumping station capacity (Cum/day) |  | cum/day |  |  | Not more than:0.561KWH/per cubic meter (cum) of plant effluent |  |  |  | - Quarterly |  |  |  | - For excess power consumption up to 5% of the Guaranteed Energy Consumption of the relevant Facility: Power Consumption Penalty: (Number of power units consumed in the relevant quarter –Guaranteed Energy Consumption for such quarter) * [Power Unit Rate] * 0.05 - For excess power consumption between 5% and 10% of the Guaranteed Energy Consumption of the relevant Facility: Power Consumption penalty: (Number of power units consumed inthe relevant quarter –Guaranteed Energy Consumption for such quarter) * [Power Unit Rate] * 0.1 - For excess power consumption above 10% of the Guaranteed Energy Consumption of the relevant Facility: Power Consumption Liquidated Damages: (Number of powerunits consumed in the relevant quarter –Guaranteed Energy Consumption for such quarter) * [Power Unit Rate]*0.25 |  |
| Chemical efficiency standards |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No | Efficiency item |  |  | Unit |  |  | Limit Value (maximum permitted average chemical use during evaluation period) |  |  |  | Efficiency evaluation period |  |  | Penalty per day as % of O&M Monthly Payment |  |
| 1 | The consumption of Chlorine during the Tests after Completion is guaranteed to be: |  |  | Kg per M3 of effluent produced |  |  | Not more than:.0.0008kg per cubic meter (cum) of plant effluent |  |  |  | - Monthly |  |  | 1% for excess of Chlorine usage |  |
| 2 | The consumption of dewatering Polymer (polyelectrolyte)during the Tests after Completion is guaranteed to be |  |  | Kg per M3 of effluent produced |  |  | Not more than:.0.0025.kg per cubic meter (cum) of plant effluent |  |  |  | - Monthly |  |  | 1% for excess of Poly electrolyte usage |  |

The performance damages listed above shall be payable in currencies indicated in the Contract Data, or, if no currencies are listed, then the damages shall be payable in the currencies and in the proportions of the Accepted Contract Amount.

The performance damages above shall be in addition to any fines that may be imposed on the Contractor by the courts in respect of pollution of the environment and/or breach of the terms of the applicable permits, licenses or consents.

# Performance Security - Option 1: Demand Guarantee

[Guarantor letterhead or SWIFT identifier code]

Beneficiary:	[insert name and Address of Employer]

Date:	[Insert date of issue]

PERFORMANCE GUARANTEE No.:	[Insert guarantee reference number]

Guarantor: 	
[Insert name and address of place of issue, unless indicated in the letterhead]

We have been informed that ________________ (hereinafter called “the Applicant”) has entered into Contract No. _____________ dated ____________ with the Beneficiary, for the execution of _____________________ (hereinafter called “the Contract”).

Furthermore, we understand that, according to the conditions of the Contract, a performance guarantee is required.

At the request of the Applicant, we as Guarantor, hereby irrevocably undertake to pay the Beneficiary any sum or sums not exceeding in total an amount of ___________ ( ),1 such sum being payable in the types and proportions of currencies in which the Contract Price is payable, upon receipt by us of the Beneficiary’s complying demand supported by the Beneficiary’s statement, whether in the demand itself or in a separate signed document accompanying or identifying the demand, stating that the Applicant is in breach of its obligation(s) under the Contract, without the Beneficiary needing to prove or to show grounds for your demand or the sum specified therein.

This guarantee shall expire, no later than the …. Day of ……, 2… 2, and any demand for payment under it must be received by us at this office indicated above on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees (URDG) 2010 Revision, ICC Publication No. 758, except that the supporting statement under Article 15(a) is hereby excluded.

_____________________ 
[signature(s)]

Note: All italicized text (including footnotes) is for use in preparing this form and shall be deleted from the final product.

# Performance Security - Option 2: Performance Bond ( Not Applicable)

By this Bond____________________ as Principal (hereinafter called “the Contractor”) and______________________________________________________________] as Surety (hereinafter called “the Surety”), are held and firmly bound unto_____________________] as Obligee (hereinafter called “the Employer”) in the amount of __________________, for the payment of which sum well and truly to be made in the types and proportions of currencies in which the Contract Price is payable, the Contractor and the Surety bind themselves, their heirs, executors, administrators, successors and assigns, jointly and severally, firmly by these presents.

WHEREAS the Contractor has entered into a written Agreement with the Employer dated the 	 day of 	, 20 	, for ___________________ in accordance with the documents, plans, specifications, and amendments thereto, which to the extent herein provided for, are by reference made part hereof and are hereinafter referred to as the Contract.

NOW, THEREFORE, the Condition of this Obligation is such that, if the Contractor shall promptly and faithfully perform the said Contract (including any amendments thereto), then this obligation shall be null and void; otherwise, it shall remain in full force and effect. Whenever the Contractor shall be, and declared by the Employer to be, in default under the Contract, the Employer having performed the Employer’s obligations thereunder, the Surety may promptly remedy the default, or shall promptly:

(1)	complete the Contract in accordance with its terms and conditions; or

(2)	obtain a Proposal or Proposals from qualified Proposers for submission to the Employer for completing the Contract in accordance with its terms and conditions, and upon determination by the Employer and the Surety of the lowest responsive Proposer, arrange for a Contract between such Proposer and Employer and make available as work progresses (even though there should be a default or a succession of defaults under the Contract or Contracts of completion arranged under this paragraph) sufficient funds to pay the cost of completion less the Balance of the Contract Price; but not exceeding, including other costs and damages for which the Surety may be liable hereunder, the amount set forth in the first paragraph hereof. The term “Balance of the Contract Price,” as used in this paragraph, shall mean the total amount payable by Employer to Contractor under the Contract, less the amount properly paid by Employer to Contractor; or

(3)	pay the Employer the amount required by Employer to complete the Contract in accordance with its terms and conditions up to a total not exceeding the amount of this Bond.

The Surety shall not be liable for a greater sum than the specified penalty of this Bond.

Any suit under this Bond must be instituted prior to the date of the issuing of the Contract Completion Certificate.

No right of action shall accrue on this Bond to or for the use of any person or corporation other than the Employer named herein or the heirs, executors, administrators, successors, and assigns of the Employer.

In testimony whereof, the Contractor has hereunto set his hand and affixed his seal, and the Surety has caused these presents to be sealed with his corporate seal duly attested by the signature of his legal representative, this 	 day of 	 20 	.

SIGNED ON 	 on behalf of

By 	 in the capacity of

In the presence of

SIGNED ON 	 on behalf of

By 	 in the capacity of

In the presence of

# Environmental and Social (ES) Performance Security

ES Demand Guarantee

[Guarantor letterhead or SWIFT identifier code]

Beneficiary:	[Insert name and Address of Employer]

Date:	[Insert date of issue]

ES PERFORMANCE GUARANTEE No.:	[Insert guarantee reference number]

Guarantor: 	
[Insert name and address of place of issue, unless indicated in the letterhead]

We have been informed that ________________ (hereinafter called “the Applicant”) has entered into Contract No. _____________ dated ____________ with the Beneficiary, for the execution of _____________________ (hereinafter called “the Contract”).

Furthermore, we understand that, according to the conditions of the Contract, a performance guarantee is required.

At the request of the Applicant, we as Guarantor, hereby irrevocably undertake to pay the Beneficiary any sum or sums not exceeding in total an amount of ___________ ( ),1 such sum being payable in the types and proportions of currencies in which the Contract Price is payable, upon receipt by us of the Beneficiary’s complying demand supported by the Beneficiary’s statement, whether in the demand itself or in a separate signed document accompanying or identifying the demand, stating that the Applicant is in breach of its Environmental and/or Social, (ES) obligation(s) under the Contract, without the Beneficiary needing to prove or to show grounds for your demand or the sum specified therein.

This guarantee shall expire, no later than the …. Day of ……, 2… 2, and any demand for payment under it must be received by us at this office indicated above on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees (URDG) 2010 Revision, ICC Publication No. 758, except that the supporting statement under Article 15(a) is hereby excluded.

_____________________ 
[signature(s)]

Note: All italicized text (including footnotes) is for use in preparing this form and shall be deleted from the final product.

# Advance Payment Security

Demand Guarantee

[Guarantor letterhead or SWIFT identifier code]

Beneficiary: 	[Insert name and Address of Employer]

Date:	[Insert date of issue]

ADVANCE PAYMENT GUARANTEE No.:	[Insert guarantee reference number]

Guarantor: 	
[Insert name and address of place of issue, unless indicated in the letterhead]

We have been informed that ________________ (hereinafter called “the Applicant”) has entered into Contract No. _____________ dated ____________ with the Beneficiary, for the execution of _____________________ (hereinafter called “the Contract”).

Furthermore, we understand that, according to the conditions of the Contract, an advance payment in the sum ___________ ( ) is to be made against an advance payment guarantee.

At the request of the Applicant, we as Guarantor, hereby irrevocably undertake to pay the Beneficiary any sum or sums not exceeding in total an amount of ___________ ( ) 1 upon receipt by us of the Beneficiary’s complying demand supported by the Beneficiary’s statement, whether in the demand itself or in a separate signed document accompanying or identifying the demand, stating either that the Applicant:

    - has used the advance payment for purposes other than the costs of mobilization in respect of the Works; or

    - has failed to repay the advance payment in accordance with the Contract conditions, specifying the amount which the Applicant has failed to repay.

A demand under this guarantee may be presented as from the presentation to the Guarantor of a certificate from the Beneficiary’s bank stating that the advance payment referred to above has been credited to the Applicant on its account number ___________ at _________________.

The maximum amount of this guarantee shall be progressively reduced by the amount of the advance payment repaid by the Applicant as specified in copies of interim statements or payment certificates which shall be presented to us. This guarantee shall expire, at the latest, upon our receipt of a copy of the interim payment certificate indicating that ninety (90) percent of the Accepted Contract Amount for Design Build, less provisional sums, has been certified for payment, or on the ___ day of _____, 2___,2 whichever is earlier. Consequently, any demand for payment under this guarantee must be received by us at this office on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees (URDG) 2010 Revision, ICC Publication No. 758, except that the supporting statement under Article 15(a) is hereby excluded.

____________________ 
[signature(s)]

Note: All italicized text (including footnotes) is for use in preparing this form and shall be deleted from the final product.

# Retention Money Security

Demand Guarantee

[Guarantor letterhead or SWIFT identifier code]

Beneficiary:	[Insert name and Address of Employer]

Date:	[Insert date of issue]

RETENTION MONEY GUARANTEE No.:	[Insert guarantee reference number]

Guarantor: 	
[Insert name and address of place of issue, unless indicated in the letterhead]

We have been informed that ________________ [insert name of Contractor, which in the case of a joint venture shall be the name of the joint venture] (hereinafter called “the Applicant”) has entered into Contract No. _____________ [insert reference number of the contract] dated ____________ with the Beneficiary, for the execution of _____________________ [insert name of contract and brief description of Works] (hereinafter called “the Contract”).

Furthermore, we understand that, according to the conditions of the Contract, the Beneficiary retains moneys up to the limit set forth in the Contract (“the Retention Money”), and that when the Commissioning Certificate has been issued under the Contract and the first half of the Retention Money has been certified for payment, payment of [insert the second half of the Retention Money or if the amount guaranteed under the Performance Guarantee when the Commissioning Certificate is issued is less than half of the Retention Money, the difference between half of the Retention Money and the amount guaranteed under the Performance Security and, if required, the ES Performance Security] is to be made against a Retention Money guarantee.

At the request of the Applicant, we, as Guarantor, hereby irrevocably undertake to pay the Beneficiary any sum or sums not exceeding in total an amount of ___________ [insert amount in figures] ( ) [amount in words]1 upon receipt by us of the Beneficiary’s complying demand supported by the Beneficiary’s statement, whether in the demand itself or in a separate signed document accompanying or identifying the demand, stating that the Applicant is in breach of its obligation(s) under the Contract, without your needing to prove or show grounds for your demand or the sum specified therein.

A demand under this guarantee may be presented as from the presentation to the Guarantor of a certificate from the Beneficiary’s bank stating that the second half of the Retention Money as referred to above has been credited to the Applicant on its account number ___________ at _________________ [insert name and address of Applicant’s bank].

This guarantee shall expire no later than the …. Day of ……, 2… 2, and any demand for payment under it must be received by us at the office indicated above on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees (URDG) 2010 Revision, ICC Publication No. 758, except that the supporting statement under Article 15(a) is hereby excluded.

____________________ 
[signature(s)]

Note: All italicized text (including footnotes) is for use in preparing this form and shall be deleted from the final product.

An individual firm is considered a domestic Proposer for purposes of the margin of preference if it is registered in the country of the Employer, has more than 50 percent ownership by nationals of the country of the Employer, and if it does not subcontract more than 10 percent of the contract price, excluding provisional sums, to foreign contractors. JVs are considered as domestic Proposer and eligible for domestic preference only if the individual member firms are registered in the country of the Employer or have more than 50 percent ownership by nationals of the country of the Employer, and the JV shall be registered in the country of the Borrower. The JV shall not subcontract more than 10 percent of the contract price, excluding provisional sums, to foreign firms. JVs between foreign and national firms will not be eligible for domestic preference.

Non-performance, as decided by the Employer, shall include all contracts where (a) non-performance was not challenged by the contractor, including through referral to the dispute resolution mechanism under the respective contract, and (b) contracts that were so challenged but fully settled against the contractor. Non-performance shall not include contracts where Employers decision was overruled by the dispute resolution mechanism. Non-performance must be based on all information on fully settled disputes or litigation, i.e. dispute or litigation that has been resolved in accordance with the dispute resolution mechanism under the respective contract and where all appeal instances available to the applicant have been exhausted.

This requirement also applies to contracts executed by the Applicant as JV member.

The Applicant shall provide accurate information on the related Application Form about any litigation or arbitration resulting from contracts completed or ongoing under its execution over the last five years. A consistent history of awards against the Applicant or any member of a joint venture may result in rejection of the Application.

If the most recent set of financial statements is for a period earlier than 12 months from the date of Application, the reason for this should be justified.

For the avoidance of doubt, a sanctioned party’s ineligibility to be awarded a contract shall include, without limitation, (i) applying for pre-qualification, expressing interest in a consultancy, and bidding, either directly or as a nominated sub-contractor, nominated consultant, nominated manufacturer or supplier, or nominated service provider, in respect of such contract, and (ii) entering into an addendum or amendment introducing a material modification to any existing contract.

A nominated sub-contractor, nominated consultant, nominated manufacturer or supplier, or nominated service provider (different names are used depending on the particular bidding document) is one which has been: (i) included by the bidder in its pre-qualification application or Proposal because it brings specific and critical experience and know-how that allow the bidder to meet the qualification requirements for the particular bid; or (ii) appointed by the Borrower.

Inspections in this context usually are investigative (i.e., forensic) in nature. They involve fact-finding activities undertaken by the Bank or persons appointed by the Bank to address specific matters related to investigations/audits, such as evaluating the veracity of an allegation of possible Fraud and Corruption, through the appropriate mechanisms. Such activity includes but is not limited to: accessing and examining a firm's or individual's financial records and information, and making copies thereof as relevant; accessing and examining any other documents, data and information (whether in hard copy or electronic format) deemed relevant for the investigation/audit, and making copies thereof as relevant; interviewing staff and other relevant individuals; performing physical inspections and site visits; and obtaining third party verification of information.

For the avoidance of doubt, a sanctioned party’s ineligibility to be awarded a contract shall include, without limitation, (i) applying for pre-qualification, expressing interest in a consultancy, and bidding, either directly or as a nominated sub-contractor, nominated consultant, nominated manufacturer or supplier, or nominated service provider, in respect of such contract, and (ii) entering into an addendum or amendment introducing a material modification to any existing contract.

A nominated sub-contractor, nominated consultant, nominated manufacturer or supplier, or nominated service provider (different names are used depending on the particular bidding document) is one which has been: (i) included by the bidder in its pre-qualification application or Proposal because it brings specific and critical experience and know-how that allow the bidder to meet the qualification requirements for the particular bid; or (ii) appointed by the Borrower.

Inspections in this context usually are investigative (i.e., forensic) in nature.  They involve fact-finding activities undertaken by the Bank or persons appointed by the Bank to address specific matters related to investigations/audits, such as evaluating the veracity of an allegation of possible Fraud and Corruption, through the appropriate mechanisms.  Such activity includes but is not limited to: accessing and examining a firm's or individual's financial records and information, and making copies thereof as relevant; accessing and examining any other documents, data and information (whether in hard copy or electronic format) deemed relevant for the investigation/audit, and making copies thereof as relevant; interviewing staff and other relevant individuals; performing physical inspections and site visits; and obtaining third party verification of information.

1	The Guarantor shall insert an amount representing the percentage of the Accepted Contract Amount specified in the Letter of Acceptance, less provisional sums, if any, and denominated either in the currency (cies) of the Contract or a freely convertible currency acceptable to the Beneficiary.

2	Insert the date twenty-eight days after the expected completion date as described in GC Clause 8.6. The Employer should note that in the event of an extension of this date for completion of the Contract, the Contractor would need to request an extension of this guarantee from the Guarantor. Such request must be in writing and must be made prior to the expiration date established in the guarantee. In preparing this guarantee, the Employer might consider adding the following text to the form, at the end of the penultimate paragraph: “The Guarantor agrees to a one-time extension of this guarantee for a period not to exceed [six months] [one year], in response to the Beneficiary’s written request for such extension, such request to be presented to the Guarantor before the expiry of the guarantee.”

1	The Guarantor shall insert an amount representing the percentage of the Accepted Contract Amount specified in the Letter of Acceptance, less provisional sums, if any, and denominated either in the currency (cies) of the Contract or a freely convertible currency acceptable to the Beneficiary.

2	Insert the date twenty-eight days after the expected completion date of design-build as described in GC Clause 9.12. The Employer should note that in the event of an extension of this date for completion of the Contract, the Employer would need to request an extension of this guarantee from the Guarantor. Such request must be in writing and must be made prior to the expiration date established in the guarantee. In preparing this guarantee, the Employer might consider adding the following text to the form, at the end of the penultimate paragraph: “The Guarantor agrees to a one-time extension of this guarantee for a period not to exceed [six months] [one year], in response to the Beneficiary’s written request for such extension, such request to be presented to the Guarantor before the expiry of the guarantee.”

1	The Guarantor shall insert an amount representing the amount of the advance payment and denominated either in the currency (ies) of the advance payment as specified in the Contract, or in a freely convertible currency acceptable to the Employer.

2 	Insert the expected Time for Completion of Design Build. The Employer should note that in the event of an extension of the time for completion of design build, the Employer would need to request an extension of this guarantee from the Guarantor. Such request must be in writing and must be made prior to the expiration date established in the guarantee. In preparing this guarantee, the Employer might consider adding the following text to the form, at the end of the penultimate paragraph: “The Guarantor agrees to a one-time extension of this guarantee for a period not to exceed [six months] [one year], in response to the Beneficiary’s written request for such extension, such request to be presented to the Guarantor before the expiry of the guarantee.”

1	The Guarantor shall insert an amount representing the amount of the second half of the Retention Money or if the amount guaranteed under the Performance Guarantee when the Commissioning Certificate is issued is less than half of the Retention Money, the difference between half of the Retention Money and the amount guaranteed under the Performance Security and denominated either in the currency(ies) of the second half of the Retention Money as specified in the Contract, or in a freely convertible currency acceptable to the Beneficiary.

2	Insert the date twenty-eight days after the Retention Period described in GC Clause 1.1.66. The Employer should note that in the event of an extension of this date for completion of the Contract, the Employer would need to request an extension of this guarantee from the Guarantor. Such request must be in writing and must be made prior to the expiration date established in the guarantee. In preparing this guarantee, the Employer might consider adding the following text to the form, at the end of the penultimate paragraph: “The Guarantor agrees to a one-time extension of this guarantee for a period not to exceed [six months] [one year], in response to the Beneficiary’s written request for such extension, such request to be presented to the Guarantor before the expiry of the guarantee.”